## Rules
OLD Rule ID | New Rule ID | Rule ID | Column4 | Column3 | Ruleset Reference | Rule Description | Applicable RMR | Rule Assertion | Comparison Value | Primary Rule | Notes | RDS Link | Evaluated? | General- P RMR = U RMR | General- P RMR = B RMR | Move to General? | Rule Dependency | Data Table Reference | Allow More Stringent? AHJ_RA_Compare | Status | Link to Draft RDS | Questions/Notes
19-1 | 19-1 | 19-1 | 19 | 1 | G3.1.2.2 | HVAC system coil capacities for the baseline building design shall be oversized by 15% for cooling and 25% for heating. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Approved | 19-1 | All questions have been addressed. RDS is ready for review. 1. Shall we split this into 2 rules that assess heating and cooling separately? Perhaps not needed as above appears to work fine. 2. Systems 1a, 1c, 9b, and 10 cannot be assessed because coils are defined at the terminal. This does not appear to impact anything though. 3. We already check that the project is modeled by orientation in Rule 5-1. The check that the sizing factors are consistent across orientations will be an umbrella check. MK: Agree that we don't have to check for this. 4. Shall I update this to only check the oversizing factor for furnaces, heat pumps, and DX cooling based on exchanges with Mike R at PNNL? MK: Agree 5. What would we expect for a 25% oversizing factor? 1.25 or 25%? MK: Not sure. The note says that 0 indicates no oversizing, so it should be either 0.25 or (more logically) 25%. CML: 0.25 is format | Check sizing factor in each of the 4 baseline RMDs. Is there an umbrella rule that checks for consistency between RMDs? Ask Jason to add column to the schema to do this check.
19-2 | 19-2 | 19-2 | 19 | 2 | G3.1.2.2 | Baseline building plant capacities shall be based on coincident loads. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Approved | 19-2 | All questions have been addressed. RDS is ready for review. Based on the email exchange with Mike R. and the logic of App G it appears that the sizing factor should apply directly to plants and that plants should be sized based on the coincidents load of the zones served. I don't think we have a way to check this. Although maybe the check at the loop level works? MK: I think this is partially taken care of by FluidLoopDesignAndControl.is_sized_using_coincident_load, but we also need oversizing_factor. I also wonder if we need is_autosized in this data group, similar to what we have in the HeatingSystem. CML: Check at the fluid loop per weekly call.
19-3 | 19-3 | 19-3 | 19 | 3 | G3.1.2.2.1 | Weather conditions used in sizing runs to determine baseline equipment capacities shall be based either on hourly historical weather files containing typical peak conditions or on design days developed using 99.6% heating design temperatures and 1% dry-bulb and 1% wet-bulb cooling design temperatures. | Baseline RMR | = | Expected Value | Applicability |  |  | Y | N | N | N |  |  |  | Not TCD required | Closed pull request | All questions have been addressed. RDS is ready for review. Don't check. Please remind me of the approach when a rule is not a primary rule, I create an RDS but the outcome is undetermined? I can also just look this up based on other RDSs. MK: Agreed. I don't think there is a way to check it. SG: Christina, I dont think there is anything you can do to determine applicability in this case, tthis rule is applicable to all buildings so the RDS can actually just be a single line that results in undetermined outcome.
19-4 | 19-4 | 19-4 | 19 | 4 | G3.1.2.2.1 | For baseline cooling sizing runs in residential dwelling units, the infiltration, occupants, lighting, gas and electricity using equipment hourly schedule shall be the same as the most used hourly weekday schedule from the annual simulation. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Approved | 19-4 | Check by looking at whether the Zone thermostat setpoint schedules match the design thermostat schedules? Actually I do not think this will work. Are there design day schedules anywhere for each zone? MK: I think this would require checking desing day schedules for infiltration, lighting, etc. Since we don't have this in the schema, I don't see how this can be checked. SG: Do we need to add a 'schedule type' which can identifyv whether a schedule is an 'annual schedule' or 'design day' schedule.? I'm not sure how easy it would be to verify this rule though. MK: It seems that if we want to check it, we'd need to add desing_heating_multiplier_schedule and desing_cooling_multiplier_scheduleto each applicable object (InteriorLighting, Infiltration, MiscellaneousEquipment) and then verify whether that schedule is equal to the typical annual schedule or 1 or 0. This rule is set to not primary which means that it would be flagged for manual review on all projects involving multifamily buildings. Perhaps it should be made primary to avoid that, assuming we are opened to adding additional schedules per above.
19-5 | 19-5 | 19-5 | 19 | 5 | G3.1.2.3 | Unmet load hours for the proposed design shall not exceed 300 (of the 8760 hours simulated). | Proposed RMR | <= | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Approved | 19-5 | I took a shot but have some questions on how to reference the output schema.
19-6 | 19-6 | 19-6 | 19 | 6 | G3.1.2.3 | Unmet load hours for the baseline design shall not exceed 300 (of the 8760 hours simulated). | Baseline RMR | <= | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Approved | 19-6 | CML: Do we check this for each rotation of the baseline model or just 0 degrees (i.e., as-designed orientation)? When I do reviews I only check the design orientation but I want to make sure that is correct.
19-10 | 19-7 | 19-7 | 19 | 7 | G3.1.2.5 and Exception 2 | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N | [5 empty] | Moved from Section 4 to end of this list
19-12 | 19-8 | 19-8 | 19 | 8 | G3.1.2.5 Exception #1 | Demand control ventilation is modeled in the baseline design in systems with outdoor air capacity greater than 3000 cfm serving areas with an average occupant design capacity greater than 100 people per 1000 ft^2. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  |  | - | Moved from Section 4 to end of this list
19-14 | 19-9 | 19-9 | 19 | 9 | G3.1.2.6 | Air economizers shall not be included in baseline HVAC Systems 1, 2, 9, and 10. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  |  | - | Moved from Section 4 to end of this list
19-15 | 19-10 | 19-10 | 19 | 10 | G3.1.2.6 | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Updated and ready for review | 19-7 | There are a number of exceptions here. Looks like we can assess #1, #2 (Zone-->air_distribution_effectiveness), NOT #3 , and for #4 not sure why this would result in different rates in the baseline and proposed? Due to sizing? MK: Yes, due to sizing, because it would be sized based on load in the baseline, but has to be 100% OA. Also, how do we want to factor in scenarios like in MF where there is just zone exhaust where the makeup air is provided via infiltration? Just check that the zone exhaust cfm is also the same in the baseline and proposed? This is a little confusing because often this is modeled with the OA CFM going through the PTACs in the baseline and then via exhaust only in the proposed. Could check if baseline OA CFM equals Exhaust CFM if OA is 0 in proposed? Maybe we could confine this to just PTAC and PTHP? MK: I don't think we should be checking for work-arounds. This RDS is about OA, so I would only check make-up air. (Is make-up air = outdoor air?) 1. When modeling demand control ventilation in the proposed design in systems with out-door air capacity less than or equal to 3000 cfm serving areas with an average design capacity of 100 people per 1000 ft2 or less. We should probably have a rule that checks that DCV is modeled in the baseline if this criteria is met. MK: I agree that this should be a separate rule. How do we determine the number of occupants? Shall we find the max across 8760 of multiplier * number_occupants. This is what I did. MK: What if system serves multiple zones? I wonder what the "average" design capacity means. Area-weighted average peak occupancy of all spaces served by the system? 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. MK: perhaps if air_distribution_effectiveness>1.0 and ventilation rates are not equal we should flag it for manual review? 3. Where the minimum outdoor air intake flow in the proposed design is provided in excess of the amount required by the building code or the rating authority, the baseline building design shall be modeled to reflect the greater of that required by either the rating authority or the building code and will be less than the proposed design. MK: this is a tough one, because it means that ventilation may be erroneously modeled the same in baseline and proposed where it needs to be a penalty. So does this mean we can never just have PASS outcome? 4. For baseline systems serving only laboratory spaces that are prohibited from recirculating return air by code or accreditation standards, the baseline system shall be modeled as 100% outdoor air.
19-20 | 19-11 | 19-11 | 19 | 11 | G3.1.2.6.1 | For systems that serve computer rooms, if the baseline system is HVAC System 11, it shall include an integrated fluid economizer meeting the requirements of Section 6.5.1.2 in the baseline building design. | Baseline RMR | = | Expected Value | Applicability |  |  | Y | N | N | N |  |  |  |  | - | What is this rule? SG: I think 19-10 just got split into 19-10 and 19-11 MK: agreed, this is just the sencond half of the sentense for 19-10, so should be merged with 19-10.
19-21 | 19-12 | 19-12 | 19 | 12 | G3.1.2.7 | The baseline system economizer high-limit shutoff shall be a dry-bulb fixed switch with set-point temperatures in accordance with the values in Table G3.1.2.7. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  | ? | Ready for review, created interpretation request | 19-8 | What is this rule? I added the DCV rule here and created a draft RDS. MK: agreed
19-22 | 19-13 | 19-13 | 19 | 13 | G3.1.2.8.1 and Exception 1 | For baseline system types 1-8 and 11-13, system design supply airflow rates shall be based on a supply-air-to-room temperature set-point difference of 20°F or the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. For systems with multiple zone thermostat setpoints, use the design set point that will result in the lowest supply air cooling set point or highest supply air heating set point. Exceptions: 1. For baseline systems serving laboratory spaces, airflow rate shall be based on a supply-air-to-room temperature set-point difference of 17°F or the required ventilation air or makeup air, whichever is greater. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  |  | - | What is this rule? SG: Recoemmnd deleting and renumbering the rules. MK: agreed
19-25 | 19-14 | 19-14 | 19 | 14 | G3.1.2.8.1 | For baseline system types 1-8 and 11-13, if return or relief fans are specified in the proposed design, the baseline building design shall also be modeled with fans serving the same functions and sized for the baseline system supply fan air quantity less the minimum outdoor air, or 90% of the supply fan air quantity, whichever is larger. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Approved | 19-9 | RDS created and ready for review.
19-28 | 19-17 | 19-15 | 19 | 15 | G3.1.2.8.2 | For baseline system types 9 & 10, the system design supply airflow rates shall be based on the temperature difference between a supply air temperature set point of 105°F and the design space-heating temperature set point, the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Updated and ready for review | 19-10 | DONE. All questions addressed. Included in RDS 19-10. I have removed the separate rules for the exceptions because they are included in this RDS. This is easy to assess, Check FanSystem --> air_economizer and Weather --> climate_zone
19-29 | 19-22 (I messed up the numbering) | 19-16 | 19 | 16 | G3.1.2.8.2 | For zones served by baseline system types 9 & 10, if the proposed design includes a fan or fans sized and controlled to provide non-mechanical cooling, the baseline building design shall include a separate fan to provide nonmechanical cooling, sized and controlled the same as the proposed design. | Baseline RMR | = | Expected Value | Applicability |  |  | Y | N | N | N |  |  |  |  | -
19-30 | 19-18 | 19-17 | 19 | 17 | G3.1.2.9 | For baseline system 1 and 2, the total fan electrical power (Pfan) for supply, return, exhaust, and relief shall be = CFMs x 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  | X, accept if fan power less than allowance |  | - | DONE. All questions addressed. Included in RDS 19-10. Do we need to keep this as a separate rule then? Include in output note for 19-15 since we do not know if gas-phase cleaning exists? MK: agreed
19-31 | 19-19 | 19-18 | 19 | 18 | G3.1.2.9 | For baseline systems 3 through 8, and 11, 12, and 13, the system fan electrical power for supply, return, exhaust, and relief shall be Pfan = bhp × 746/fan motor efficiency. Where, bhp = brake horsepower of baseline fan motor from Table G3.1.2.9; fan motor efficiency = the efficiency from Table G3.9.1 for the next motor size greater than the bhp using a totally enclosed fan cooled motor at 1800 rpm | Baseline RMR | = | Expected Value | Applicability |  |  | Y | N | N | N |  |  | X, accept if fan power less than allowance |  | - | DONE. All questions addressed. Included in RDS 19-10. Do we need to keep this as a separate rule then? Check if the BuildingSegment --> lighting_building_area_type is Retail and Building-->refrigerated_case is not null? If yes then do not flag if no economizer if proposed does not have economizer? SG: this makes sense to me. MK: agreed
19-32 | 19-20 | 19-19 | 19 | 19 | G3.1.2.9 | For baseline systems 9 and 10 the system fan electrical power (Pfan) for supply, return, exhaust, and relief shall be CFMs × 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm. If modeling a non-mechanical cooling fan is required by Section G3.1.2.8.2, there is a fan power allowance of Pfan = CFMnmc × 0.054, where, CFMnmc = the baseline non-mechanical cooling fan airflow, cfm for the non-mechanical cooling. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  | X, accept if fan power less than allowance |  | - | Included in RDS 19-10. Do we need to keep this as a separate rule then?
19-34 | 19-23 | 19-20 | 19 | 20 | G3.1.2.9 | The calculated system fan power shall be distributed to supply, return, exhaust, and relief fans in the same proportion as the proposed design. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Updated and ready for review. | 19-11 | Make non -primary since it won't apply to many projects and only a few systems in applicable projects. 1. Serve computers rooms? Primarily or if any space is a computer room? May also need to update 19-10 depending on decision. System 11 should always serve computer rooms if assigned correctly which is assessed elsewhere. 2. Which loop would the integrated waterside economizer be on? The primary or secondary chilled water loop? The CW loop? Straightforward check except we will not be able to assess whether it meets the reqs in Section 6.5.1.2 as far as I can tell. MK: agreed
19-35 | 19-24 | 19-21 | 19 | 21 | G3.1.2.10 | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Ready for review | 19-12 | Straightforward: AirEconomizer-->high_limit_shutoff_temperature
19-36 | 19-25 | 19-22 | 19 | 22 | G3.1.2.10 | Baseline systems modeled with exhaust air energy recovery shall allow bypass for economizer control where applicable. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Ready for review but question about the way to handle labs. See RDS for the approach used. | 19-13 | Wait for more group members for discussion. Add data elements for accomplishing this? Boolean, autosized? And the supply air temperature setpoint used for sizing heating and cooling. This RDS is in progress but I hit a road block because below appear to be the relevant data elements but I am not sure how to assess this given the supply temperatures will be different depending on whether heating or cooling is needed. This applies to both MZ systems with reheat and single zone systems without reheat. For a single zone system the supply air temperature setpoint could be 55F for cooling and 90F for heating. A similar logic would apply to the terminal setpoint. Unless I should use heating_system.heating_coil_setpoint (there is no analogous cooling_system_cooling_coil_setpoint) but this would be odd. FanSystem.supply_air_setpoint_temperature Terminal.supply_setpoint_temperature Use Zone --> design_thermostat setpoint and FanSystem --> supply_air_setpoint_temperature to assess a delta T of 20F. In the note if fail perhaps we can include the exceptions. Or do we check that the OA requirement is and if the cfm matches that then also pass? SG: I think just the first check and if the building doesnt pass base don the 20F difference, then undetermined with Manual Review required. MK: This logic does not verify whether the flow rate is auto-sized. Perhaps we need to add Fan.is_autosized.
N/A | 19-26 | 19-23 | 19 | 23 | G3.1.2.2.1 | For cooling sizing runs, schedules for internal loads, including those used for infiltration, occupants, lighting, gas and electricity using equipment, shall be equal to the highest hourly value used in the annual simulation runs and applied to the entire design day. For heating sizing runs, schedules for internal loads, including those used for occupants, lighting, gas and electricity using equipment, shall be equal to the lowest hourly value used in the annual simulation runs, and schedules for infiltration shall be equal to the highest hourly value used in the annual simulation runs and applied to the entire design day. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  |  | - | What is this rule?- Please delete.
4-3 | 19-27 | 19-24 | 19 | 24 | Table G3.1 Section 4 & G3.1.2.4 | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the proposed design. | Proposed RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  |  | - | I think we can access this because it refers to the design thermostat setpoint. I incorporated into 19-13 which is in progress. I don't think we can assess this, where is this in the standard? SG: G3.1.2.8.1 MK: I agree. The rule would apply to all systems that serve zones that have differing design thermostat setpoints. So all such systems will be flagged for manual review.
4-12 | 19-28 | 19-25 | 19 | 25 | Table G3.1 Section 4 & G3.1.2.4 | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the baseline design. | Baseline RMR | = | Expected Value | Full | Added tentative Rule 4-12 below Exceptions: 1. Spaces where no heating and/or cooling system is to be installed. |  | Y | N | N | N |  |  |  | Ready for review with questions in the RDS. | 19-14 | Next step: Discuss plan for this one. For each thermal zone in the proposed quantify the supply, return, exhaust, and relief fan power per zone (Q1 how to apportion this per zone, based on terminal fan cfm?) ? Do the same for the baseline and compare. I think at least small mismatches will be VERY likely. I have always found his rule tricky since there is not a one to one match between HVAC systems between the baseline and proposed. I think these calculations are difficult for modelers. What about exhaust fan? I think this is doable just would like to discuss how the zonal exhaust would fit into this. SG: Is reliefe fan same as exhaust fan? MK: Yes, I would check that all fan types align between baseline and proposed. It may get tricky though because zone to system grouping may be different in the baseline vs proposed.
4-5 | 19-29 | 19-26 | 19 | 26 | Table G3.1 Section 4 & G3.1.2.4 | HVAC fans shall remain on during unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements during unoccupied hours in the proposed design. | Proposed RMR | = | Expected Value | Full | None |  | Y | N | N | N |  |  |  | Strikethrough because covered in 19-13? | Covered in 19-13 | Use Zone --> design_thermostat setpoint and FanSystem --> supply_air_setpoint_temperature to assess a delta T of 17F. Check if labs are served. In the note if fail perhaps we can include the exceptions. Or do we check that the OA requirement is and if the cfm matches that then also pass? MK: same comment as for 19-22. I would either check for OA or perhaps just make this a non-mandatory rule because it applies only to labs.
4-14 | 19-30 | 19-27 | 19 | 27 | Table G3.1 Section 4 & G3.1.2.4 | HVAC fans shall remain on during unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements during unoccupied hours in the baseline design. | Baseline RMR | = | Expected Value | Full | None |  | Y | N | N | N
4-8 | 19-31 | 19-28 | 19 | 28 | Table G3.1 Section 4 & G3.1.2.4 | Schedules for HVAC fans that provide outdoor air for ventilation excluding unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements shall be cycled ON and OFF to meet heating and cooling loads during unoccupied hours in the proposed design. | Proposed RMR | = | Expected Value | Full | None |  | Y | N | N | N |  |  |  | There is an outstanding question on Github. | 19-17 | RDS created but Maria's point remains about a fan_autosized data element. Straightforward MK: same commend as for 19-22.
4-16 | 19-32 | 19-29 | 19 | 29 | Table G3.1 Section 4 & G3.1.2.4 | Schedules for HVAC fans that provide outdoor air for ventilation excluding unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements shall be cycled ON and OFF to meet heating and cooling loads during unoccupied hours in the baseline design. | Baseline RMR | = | Expected Value | Full |  |  | Y | N | N | N |  |  |  | Ready for review | 19-22 | Add element to schema to identify that there is non-mechanical cooling per phone call. Add an issue. Looks like we may actually have this already for cooling type. Would this be a separate HVAC system? Should we include this in the baseline HVAC system function? Look for an HVAC system with just a fan to represent this? Need to discuss with team how this would show up in the schema. SG: Should discuss MK: perhaps add FanSystem.non_mechanical_cooling_fans? Not sure how it will be modeled though. Perhaps add this field and make the RDS non-mandatory
4-10 | 19-33 | 19-30 | 19 | 30 | Section G3.1.2.4 Exception #1 | For Systems 6 and 8, only the terminal-unit fan and reheat coil shall be energized to meet heating set point during unoccupied hours in the baseline design. | Baseline RMR | = | Expected Value | Applicability | None |  | Y | N | N | N | Rule 18 |  |  | Approved | 19-18
4-6 | 19-34 | 19-31 | 19 | 31 | Table G3.1 Section 4 Exception #3 | HVAC fans shall remain on during unoccupied hours in systems primarily serving computer rooms in the proposed design. | Proposed RMR | = | Expected Value | Full | None |  | Y | N | N | N |  |  |  | Updated but there are some discussion items for next call. | 19-19 | RDS created per below. I don't think we can assess this because the schema does not appear to collect information about pressure drop adjustments. Maybe we could check with the assumption of there being none and if the fan power aligns with that then pass and if its greater than undetermined? MK: Perhaps check whether the fan power is as expected without any pressure drop adjustments except for baseline energy recovery? This rule applies to all systems, so making it non-mandatory with produce as many flags as HVAC systems, which is undesirable.
4-15 | 19-35 | 19-32 | 19 | 32 | Table G3.1 Section 4 Exception #3 | HVAC fans shall remain on during unoccupied hours in systems primarily serving computer rooms in the baseline design. | Baseline RMR | = | Expected Value | Full | None |  | Y | N | N | N |  |  |  | Ready for review | 19-20 | Ready for review
4-4 | 19-36 | 19-33 | 19 | 33 | Table G3.1 Section 4 Exception #1 | Where no heating and/or cooling system is to be installed, and a heating or cooling system is being simulated only to meet the requirements described in this table, heating and/or cooling system fans shall not be simulated as running continuously during occupied hours but shall be cycled ON and OFF to meet heating and cooling loads during all hours in the proposed design. | Proposed RMR | = | Expected Value | Applicability | None |  | Y | N | N | N |  |  |  | Archived, combined with 19-20. | 19-21 | Discuss with team MK: I would make it non-mandatory - see 19-29.
4-13 | 19-37 | 19-34 | 19 | 34 | Table G3.1 Section 4 Exception #1 | Where no heating and/or cooling system is to be installed, and a heating or cooling system is being simulated only to meet the requirements described in this table, heating and/or cooling system fans shall not be simulated as running continuously during occupied hours but shall be cycled ON and OFF to meet heating and cooling loads during all hours in the baseline design. | Baseline RMR | = | Expected Value | Applicability | None |  | Y | N | N | N |  |  |  | Ready for review | 19-23
New | 19-39 | 19-35 | 19 | 35 | G3.1.2.5 Exception #4 | For baseline systems serving only laboratory spaces that are prohibited from recirculating return air by code or accreditation standards, the baseline system shall be modeled as 100% outdoor air. Rule only applies when baseline outdoor air CFM is modeled as greater than proposed design outdoor air CFM. | Baseline RMR | = | Expected Value | Applicability |  |  | Y | N | N | N |  |  |  | Ready for review | 19-24 | Ready for review We can check, should we try and check the exceptions? Looks like we can check some but some others not sure if we can since energy recovery is not specified for heating and cooling separately (exceptions 4 and 5). MK: I would check for the checkable exceptions, and flag the rest for manual review. 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design.
New | 19-40 | 19-36 | 19 | 36 | G3.1.2.10 | Baseline systems required to model energy recovery per G3.1.2.10 shall be modeled with a 50% enthalpy recovery ratio. | Baseline RMR | = | Expected Value | Applicability |  | Yet to be reviewd/merged | Y | N | N | N |  |  |  | Ready for review | 19-25 | Ready for review I think this involves checking that EnergyRecoveryOperationOptions = When_Minimum_Outside_Air. Agreed? MK: Yes
19-17 | 19-11 |  |  |  | G3.1.2.6 | Proposed building system has a gas phase air cleaner and no economizer has been modeled in the baseline building system. | Baseline RMR | = | Expected Value | No |  |  | Y | N | N | N |  |  |  | Ready for review | 19-26
19-18 | 19-12 |  |  |  | G3.1.2.7 | Proposed system serves a supermarket with open refrigerated casework systems and baseline system has not been modeled with an economizer | Baseline RMR | = | Expected Value | Yes |  |  | Y | N | N | N |  |  |  | Ready for review | 19-27
19-19 | 19-13 |  |  |  | G3.1.2.8.1 | Proposed building system serves computer rooms and baseline system is HVAC system type 3 or 4., which shall not be modeled with an economizer. | Baseline RMR | = | Expected Value | Yes |  |  | Y | N | N | N |  |  |  | Ready for review | 19-28
19-26 | 19-15 |  |  |  | #1 Exception to G3.1.2.8.1 | For baseline system types 1-8 and 11-13, for systems serving laboratory spaces, airflow rate shall be based on a supply-air-to-room temperature set-point difference of 17°F or the required ventilation air or makeup air, whichever is greater | Baseline RMR | = | Expected Value | Yes |  |  | Y | N | N | N |  |  |  | Ready for review | 19-29
19-27 | 19-16 |  |  |  | #2 Exception to G3.1.2.8.1 | For baseline system types 1-8, 11-13, if the proposed design HVAC system airflow rate based on latent loads is greater than the design airflow rate based on sensible loads, then the same supply-air-to-room-air humidity ratio difference (gr/lb) used to calculate the proposed design airflow shall be used to calculate design airflow rates for the baseline building design. | Baseline RMR | = | Expected Value | No |  |  | N | N | N | N |  |  |  | Ready for review | 19-30
19-24 | 19-17 |  |  |  | G3.1.2.8.2 | For systems with multiple zone thermostat set points, use the design set point that will result in the lowest supply air cooling set point or highest supply air heating set point. | Baseline RMR | = | Expected Value | No |  |  | Y | N | N | N |  |  |  | Ready for review | 19-31
19-33 | 19-21 |  |  |  | G3.1.2.9 | For Systems 9 and 10, if modeling a non-mechanical cooling fan is required by Section G3.1.2.8.2, there is a fan power allowance of Pfan = CFMnmc × 0.054, where, CFMnmc = the baseline non-mechanical cooling fan airflow, cfm for the non-mechanical cooling. | Baseline RMR | = | Expected Value | No |  |  | Y | N | N | N |  |  |  | Ready for review | 19-32
New | 19-38 |  |  |  | G3.1.2.5 Exception #3 | Where the minimum outdoor air intake flow in the proposed design is provided in excess of the amount required by the building code or the rating authority, the baseline building design shall be modeled to reflect the greater of that required by either the rating authority or the building code and will be less than the proposed design. | Baseline RMR | = | Expected Value | No |  |  | N | N | N | N |  |  |  | Ready for review | 19-33
19-7 | Assessed in 4-3, 4-15 (new 4-12), 4-17 (new-4-14), 4-19 (new 4-16) and 4-10 |  |  |  | G3.1.2.4 | For the baseline and proposed building systems, the supply and return fans shall operate continuously whenever HVAC zones are occupied and shall be cycled to meet heating and cooling loads during unoccupied hours. | Baseline RMR | = | Expected Value | Yes |  |  | Y | N | N | N |  |  |  | Ready for review | 19-34
19-8 | This is already assessed in Rule 4-5. |  |  |  | G3.1.2.4 | For the baseline and proposed systems, the supply, return, and/or exhaust fans will remain on during occupied and unoccupied hours in HVAC zones that have health and safety mandated minimum ventilation requirements during unoccupied hours. | Baseline RMR | = | Expected Value | Yes |  |  | Y | N | N | N |  |  |  | Ready for review | 19-35
19-9 | This is included in 4-12 (new 4-10) which we made not a primary rule because there was some difficulty with assessing it. SG: We should then remove this rule f |  |  |  | G3.1.2.4 | For baseline systems 6 and 8, only the terminal-unit fan and reheat coil shall be energized to meet heating set point during unoccupied hours and the main supply fan shall remain off (unless there is a cooling load?) | Baseline RMR | = | Expected Value | No |  |  | Y | N | N | N
19-11 | Removed |  |  |  | G3.1.2.6 | design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. | Baseline RMR | = | Expected Value |  |  |  | Y | N | N | N |  |  |  | Ready for review | 19-36
19-13 | Removed |  |  |  | G3.1.2.6 |  | Baseline RMR | = | Expected Value |  |  |  | Y | N | N | N |  |  |  | Ready for review | 19-37
19-16 | Removed |  |  |  | G3.1.2.6 | 0 | Baseline RMR | = | Expected Value |  |  |  | Y | N | N | N |  |  |  | Not evaluated | None
19-23 | Removed |  |  |  | G3.1.2.8.1 | Baseline System Types 1-8, 11-13 | Baseline RMR | = | Expected Value |  |  |  | Y | N | N | N |  |  |  | Ready for review | 19-39

## Rules-Nonmandatory (hidden)
Rule ID | Ruleset Reference | Rule Description | Applicable RMR | Rule Assertion | Comparison Value | Rule Dependency | Mandatory Rule | Notes
22-1 | - | Design CHW Loop Supply Temperature = 44F | Baseline RMR | = | Expected Value | none | Yes
22-2 | - | Design CHW Loop Return Temperature = 56F | Baseline RMR | = | Expected Value | none | Yes
22-3 | - | CHW Loop temperature reset = OA Reset | Baseline RMR | = | Expected Value | none | Yes
22-4 | - | CHW Loop temepratrue reset schedule values are correct. | Baseline RMR | = | Expected Value | none | Yes
22-5 | - | CHW Loop temperature reset = Load Reset when it serves an AHU of System Type 11. | Baseline RMR | = | Expected Value | none | Yes
22-6 | - | CHW Loop Max reset Temp is 54F when Rule 5 is true | Baseline RMR | = | Expected Value | rule 5 is True | Yes
22-7 | - | CHW Loop has a secondary pump | Baseline RMR | = | Expected Value | none | Yes
22-8 | - | Secondary Pump speed control = VFD when loop capacity >=300 tons | Baseline RMR | = | Expected Value | rule 8 is true | Yes
22-9 | - | Secondary pump min flow setpoint is 25% when rule 8 | Baseline RMR | = | Expected Value | none | Yes
22-10 | - | Secondary pump speed control = ride curve when loop capacity < 300 tons | Baseline RMR | = | Expected Value | none | Yes
22-11 | - | Secondary pump power = 13W/gpm | Baseline RMR | = | Expected Value | none | Yes
18-1 | G3.1.3.9 | One exception for chilled water temperature reset based on OA is when the chilled water is purchased. | Baseline RMR | = | Expected Value | none | No
18-2 | G3.1.3.10 | Purchased CHW loop has a distribution pump (T/F) | Baseline RMR | = | Expected Value | none | No
18-3 | G3.1.3.10 | Purchased CHW loop distribution pump speed control is a VFD | Baseline RMR | = | Expected Value | Rule 13 is true | No
18-4 | G3.1.3.10 | Purchased CHW loop distribution pump minimum flow setpoint = 25% | Baseline RMR | = | Expected Value | Rule 13 is true | No
18-5 | G3.1.3.10 | Purchased CHW loop distribution pump power is 16W/gpm | Baseline RMR | = | Expected Value | Rule 13 is true | No
22-12 | G3.1.3.11 | Heat Rejection loop has a single heat rejection device attached? (T/F) | Baseline RMR | = | Expected Value | none | No
22-13 | G3.1.3.11 | Heat Rejection device type = axial fan | Baseline RMR | = | Expected Value | Rule 17 is true | No
22-14 | - | Heat rejection Device Range = 10 degrees | Baseline RMR | = | Expected Value | Rule 17 is true | Yes
22-15 | - | Design Wet Bulb is 12.8C<=WB<=32.2C? (55F->90F) | Baseline RMR | = | Expected Value | Rule 17 is true | Yes
22-16 | - | Heat Rejection Device Approach calaculated correctly (T/F) | Baseline RMR | = | Expected Value | Rule 36 is true | Yes
22-17 | - | Heat Rejection Design Supply Temperature is correct | Baseline RMR | = | Expected Value | Rule 36 is true | Yes
22-18 | G3.1.3.11 | Heat Rejection fan power = 3.47 L/s-kW (38.2 gpm/hp) | Baseline RMR | = | Expected Value | Rule 36 is true | No
22-19 | G3.1.3.11 | Heat Rejection fan speed control = VFD? | Baseline RMR | = | Expected Value | Rule 36 is true | No
22-20 | - | Heat Rejection Loop temperature reset = Load Reset | Baseline RMR | = | Expected Value | none | Yes
22-21 | - | Miinimum condenser water reset temp is per Table G3.1.3.11? | Baseline RMR | = | Expected Value | Rule 23 is true | Yes
22-22 | - | Chiller Type is correct per Table G3.1.3.7? | Baseline RMR | = | Expected Value | none | Yes
22-23 | - | Chiller efficiency is correct per Table G3.5.3 | Baseline RMR | = | Expected Value | none | Yes
22-24 | - | Chiller has an associated primary pump? | Baseline RMR | = | Expected Value | none | Yes
22-25 | - | Primary pump sepeed control = constant | Baseline RMR | = | Expected Value | rule 27 is true | Yes
22-26 | - | Primary pump power = 9W/gpm | Baseline RMR | = | Expected Value | Rule 27 is true and Loop doesn't serve System 11 | Yes
22-27 | - | Primary pump power = 12W/gpm | Baseline RMR | = | Expected Value | Rule 27 is true and Loop serves system 11 | Yes
22-28 | - | Chiller has an associated condenser pump? | Baseline RMR | = | Expected Value | none | Yes
22-29 | - | Condenser pump speed control = constant | Baseline RMR | = | Expected Value | Rule 31 is true | No
22-30 | - | Condenser pump power is 19W/gpm | Baseline RMR | = | Expected Value | Rule 31 is true and loop does not serve system type 11 | Yes
22-31 | - | Distribution pump power is 22W/gpm | Baseline RMR | = | Expected Value | Rule 31 is true and loop serves system type 11 | Yes
22-32 | - | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR | = | Expected Value | none | Yes
22-33 | - | Chiller capacity is correct | Baseline RMR | = | Expected Value | Rule 37 is true | No
18-6 | G3.1.3.8 | Purchased CHW design supply temperature = 44 | Baseline RMR | = | Expected Value |  | No
18-7 | G3.1.3.8 | Purchased CHW design return temp = 56 | Baseline RMR | = | Expected Value |  | No
18-8 | - | For systems using purchased chilled water, the cooling source shall be modeled as purchased chilled water in both the proposed design and baseline building design. On-site chillers and direct expansion equipment shall not be modeled in the baseline building design. | Baseline RMR | = | Expected Value |  | Yes
22-34 | - | Baseline must only have no more than one CHW plant | Baseline RMR | = | Expected Value |  | Yes
22-35 | - | CHW plant capacities shall be based on coincident loads. | Baseline RMR | = | Expected Value |  | Yes
18-9 | - | Baseline chilled water system that uses purchased chilled water shall be modeled with building distribution loop only. | Baseline RMR | = | Expected Value
Note on G15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule 18-3 is true
Note on G16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule 18-3 is true
Note on G17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule 18-3 is true
Note on B35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Did not find these two
Note on A40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Maybe 22-1 and 22-2 could cover these two?

## Templates
key1 | key2 | key3 | key4 | data_group | object_id | parent_id | data_element | unit_type | units | Generic Airside | System_1_PTAC | System_1a_PTAC | System_1b_PTAC | System_1c_PTAC | System_2_PTHP | System_3_PSZ_AC_Gas_Furnace | System_3a_PSZ_AC_Gas_Furnace | System_3b_PSZ_AC_Gas_Furnace | System_3c_PSZ_AC_Gas_Furnace | System_4_PSZ_HP | System_5_PVAV_HW_Reheat | System_5b_PVAV_HW_Reheat | System_6_PVAV_Elec_Reheat | System_6b_PVAV_Elec_Reheat | System_7_VAV_HW_Reheat | System_7a_VAV_HW_Reheat | System_7b_VAV_HW_Reheat | System_7c_VAV_HW_Reheat | System_8_PFP_Reheat | System_8a_PFP_Reheat | System_8b_PFP_Reheat | System_8c_PFP_Reheat | System_9_Warm_Air_Furnace_Gas | System_9b_Warm_Air_Furnace_Gas | System_10_Heating_Resistance_Elec | System_11.1_VAV_SZ | System_11.1a_VAV_SZ | System_11.1b_VAV_SZ | System_11.1c_VAV_SZ | System_11.2_VAV_SZ | System_11.2a_VAV_SZ | System 12_CAV_SZ_HW | System 12a_CAV_SZ_HW | System 12b_CAV_SZ_HW | 19_4_template_system_7a
id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
weather | climate_zone |  |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone
calendar | day_of_week_for_january_1 |  |  | ASHRAE229 | ASHRAE229 1 | calendar | day_of_week_for_january_1 | [37 empty] | SUNDAY
ruleset_model_descriptions[0] | id |  |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1
JSON_PATH:buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1
JSON_PATH:buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | Air Terminal | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTHP Terminal 1 | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | VAV Air Terminal 1
JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | true | false | false | false | false | false | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true
JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME
JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_systems |  |  | Airside System 1 | PTAC 1 | PTAC 1 | PTAC 1 | PTAC 1 | PTHP 1 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 4 | System 5 | System 5 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 8 | System 8 | System 8 | System 8 | System 9 | System 9B | System 10 | System 11 | System 11 | System 11 | System 11 | System 11 | System 11 | System 12 | System 12 | System 12 | System 7
JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  |  |  | HOT_WATER |  | HOT_WATER | [6 empty] | HOT_WATER | HOT_WATER | ELECTRIC | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | ELECTRIC | ELECTRIC | HOT_WATER | HOT_WATER |  | HOT_WATER | ELECTRIC | [9 empty] | HOT_WATER
JSON_PATH:zones[0] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  |  |  | Boiler Loop 1 |  | Purchased HW Loop 1 | [6 empty] | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | [10 empty] | Boiler Loop 1
JSON_PATH:zones[0] | terminals[0] | cooling_source |  | Air Terminal | Terminal 1 | Zone 1 | cooling_source |  |  |  |  | CHILLED_WATER |  | CHILLED_WATER
JSON_PATH:zones[0] | terminals[0] | cooling_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | cooling_from_loop |  |  |  |  | Purchased CHW Loop 1 |  | Purchased CHW Loop 1
JSON_PATH:zones[0] | terminals[0] | fan | id | Air Terminal | Terminal 1 | Zone 1 | fan |  |  |  |  | Fan 1 |  | Fan 1 | [8 empty] | Fan 1 | Fan 1 |  |  |  |  | Fan 1 | Fan 1 | Fan 1 | Fan 1 |  | Terminal Fan 1 | Terminal Fan 1
JSON_PATH:zones[0] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 1 | Zone 1 | fan_configuration | [15 empty] | PARALLEL | PARALLEL |  |  |  |  | PARALLEL | PARALLEL | PARALLEL | PARALLEL
JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id | [13 empty] | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | [12 empty] | Thermal Zone 2
JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule | [13 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [12 empty] | Required Cooling Schedule 1
JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule | [13 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | [12 empty] | Required Heating Schedule 1
JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id | [13 empty] | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | [12 empty] | VAV Air Terminal 2
JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration | [13 empty] | true | true | true | true | TRUE | true | true | true | true | true | true | true | [12 empty] | true
JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type | [13 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [12 empty] | VARIABLE_AIR_VOLUME
JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_systems | [13 empty] | System 5 | System 5 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 8 | System 8 | System 8 | System 8 | [12 empty] | System 7
JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source | [13 empty] | HOT_WATER | HOT_WATER | ELECTRIC | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | ELECTRIC | ELECTRIC | HOT_WATER | HOT_WATER | [12 empty] | HOT_WATER
JSON_PATH:zones[1] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop | [13 empty] | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | [12 empty] | Boiler Loop 1
JSON_PATH:zones[1] | terminals[0] | cooling_source |  | Air Terminal | Terminal 2 | Zone 2 | cooling_source
JSON_PATH:zones[1] | terminals[0] | cooling_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | cooling_from_loop
JSON_PATH:zones[1] | terminals[0] | fan | id | Air Terminal | Terminal 2 | Zone 2 | fan | [15 empty] | Fan 2 | Fan 2 |  |  |  |  | Fan 2 | Fan 2 | Fan 2 | Fan 2
JSON_PATH:zones[1] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration | [15 empty] | PARALLEL | PARALLEL |  |  |  |  | PARALLEL | PARALLEL | PARALLEL | PARALLEL
JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | Airside System 1 | PTAC 1 | PTAC 1 | PTAC 1 | PTAC 1 | PTHP 1 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 4 | System 5 | System 5 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 8 | System 8 | System 8 | System 8 | System 9 | System 9B | System 10 | System 11 | System 11 | System 11 | System 11 | System 11 | System 11 | System 12 | System 12 | System 12 | System 7
JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | Cooling System 1 | DX Coil 1 |  | DX Coil 1 |  | HP Cooling Coil 1 | DX Coil 1 | Cooling Coil 1 | DX Coil 1 | Cooling Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 |  |  |  | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1
JSON_PATH:cooling_system | type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  |  | DIRECT_EXPANSION |  | DIRECT_EXPANSION |  | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP |  |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP
JSON_PATH:cooling_system | chilled_water_loop |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop | [9 empty] | Purchased CHW Loop 1 |  | Purchased CHW Loop 1 | [5 empty] | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 |  |  |  | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1
JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  | Heating System 1 | HHW Coil 1 |  | HHW Coil 1 |  | HP Heating Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | HP Coil 1 | [12 empty] | Furnace Coil 1 |  | Heating Coil 1 | Heating Coil 1 | Heating Coil 1 | HHW Coil 1 | HHW Coil 1 | Boiler Coil 1 | Boiler Coil 1 | Boiler Coil 1 | Boiler Coil 1 | HHW Coil 1
JSON_PATH:heating_system | type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  |  | FLUID_LOOP |  | FLUID_LOOP |  | HEAT_PUMP | FURNACE | FURNACE | FLUID_LOOP | FLUID_LOOP | HEAT_PUMP | [12 empty] | FURNACE |  | FURNACE | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP
JSON_PATH:heating_system | energy_source_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type | [25 empty] | NATURAL_GAS |  | ELECTRICITY
JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  |  | Boiler Loop 1 |  | Purchased HW Loop 1 |  |  |  |  | Purchased HW Loop 1 | Purchased HW Loop 1 | [18 empty] | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1
JSON_PATH:preheat_system | id |  |  | PreheatSystem | Heating System 1 | HVAC 1 | id | [13 empty] | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | [12 empty] | Preheat Coil 1
JSON_PATH:preheat_system | type |  |  | PreheatSystem | Heating System 1 | HVAC 1 | heating_system_type | [13 empty] | FLUID_LOOP | FLUID_LOOP | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | [12 empty] | FLUID_LOOP
JSON_PATH:preheat_system | hot_water_loop |  |  | PreheatSystem | Heating System 2 | HVAC 1 | hot_water_loop | [13 empty] | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  |  | Purchased HW Loop 1 | Purchased HW Loop 1 | [12 empty] | Boiler Loop 1
JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | Fan System 1 | CAV Fan System 1 |  | CAV Fan System 1 |  | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 |  | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1
JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  |  | CONSTANT |  | CONSTANT |  | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT |  | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE
JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | Supply Fan 1 |  | Supply Fan 1 |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1
JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1 | [5 empty] | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1
JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  |  | Boiler 1 | Boiler 1 | [8 empty] | Boiler 1 |  |  |  | Boiler 1 | Boiler 1 |  |  | Boiler 1 | Boiler 1 | [9 empty] | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1
JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  |  | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | [9 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1
JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  |  | NATURAL_GAS | NATURAL_GAS | [8 empty] | NATURAL_GAS |  |  |  | NATURAL_GAS | NATURAL_GAS |  |  | NATURAL_GAS | NATURAL_GAS | [9 empty] | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS
JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id | [17 empty] | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  |  |  |  | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  | Chiller 1
JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop | [17 empty] | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1
JSON_PATH:chillers[0] | design_capacity |  |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[0] | energy_source_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type
JSON_PATH:chillers[0] | full_load_efficiency |  |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton
JSON_PATH:chillers[0] | compressor_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type
JSON_PATH:chillers[1] | id |  |  | Chiller | Chiller 2 | ASHRAE229 1 | id
JSON_PATH:chillers[1] | cooling_loop |  |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[1] | design_capacity |  |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[2] | id |  |  | Chiller | Chiller 3 | ASHRAE229 1 | id
JSON_PATH:chillers[2] | cooling_loop |  |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[2] | design_capacity |  |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[3] | id |  |  | Chiller | Chiller 4 | ASHRAE229 1 | id
JSON_PATH:chillers[3] | cooling_loop |  |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[3] | design_capacity |  |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:external_fluid_sources[0] | id |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | id |  |  |  |  | Purchased CHW 1 | Purchased HW 1 | Purchased HW 1 |  |  | Purchased CHW | Purchased HW | Purchased CHW |  |  | Purchased HW 1 |  | Purchased HW 1 |  | Purchased CW 1 | Purchased HW 1 | Purchased HW 1 |  | Purchased CW 1 | Purchased HW 1 | Purchased HW 1 |  | Purchased HW 1 |  |  | Purchased CW 1 | Purchased HW 1 | Purchased HW 1 |  | Purchased CW 1 |  | Purchased CW 1 | Purchased HW 1 | Purchased CW 1
JSON_PATH:external_fluid_sources[0] | loop |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | loop |  |  |  |  | Purchased CHW Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  |  | Purchased CHW Loop 1 | Purchased HW Loop 1 | Purchased CHW Loop 1 |  |  | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  |  | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Chilled Water Loop 1 |  | Chilled Water Loop 1 | Purchased HW Loop 1 | Chilled Water Loop 1
JSON_PATH:external_fluid_sources[0] | type |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | type |  |  |  |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  |  | CHILLED_WATER | HOT_WATER | CHILLED_WATER |  |  | HOT_WATER |  | HOT_WATER |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  | HOT_WATER |  |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  | CHILLED_WATER |  | CHILLED_WATER | HOT_WATER | CHILLED_WATER
JSON_PATH:external_fluid_sources[1] | id |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | id | [6 empty] | Purchased CHW 1 |  |  |  |  | Purchased HW | [8 empty] | Purchased CW 1 |  |  |  | Purchased CW 1 | [6 empty] | Purchased CW 1
JSON_PATH:external_fluid_sources[1] | loop |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | loop | [6 empty] | Purchased CHW Loop 1 |  |  |  |  | Purchased HW Loop 1 | [8 empty] | Chilled Water Loop 1 |  |  |  | Chilled Water Loop 1 | [6 empty] | Chilled Water Loop 1
JSON_PATH:external_fluid_sources[1] | type |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | type | [6 empty] | CHILLED_WATER |  |  |  |  | HOT_WATER | [8 empty] | CHILLED_WATER |  |  |  | CHILLED_WATER | [6 empty] | CHILLED_WATER
JSON_PATH:heat_rejections[0] | id |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id
JSON_PATH:heat_rejections[0] | loop |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop
JSON_PATH:heat_rejections[0] | type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type
JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
JSON_PATH:heat_rejections[0] | design_water_flowrate |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min
JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
JSON_PATH:heat_rejections[0] | fan_speed_control |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control
JSON_PATH:heat_rejections[0] | range |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature_difference | R
JSON_PATH:heat_rejections[0] | reset_type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type
JSON_PATH:heat_rejections[1] | id |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id
JSON_PATH:heat_rejections[1] | loop |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | loop
JSON_PATH:heat_rejections[1] | type |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | type
JSON_PATH:pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id | [13 empty] | Boiler Pump 1 | HW Pump 1 |  | HW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | HW Pump 1 | HW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | HW Pump 1 | HW Pump 1 |  | HW Pump 1 |  | Chiller Pump 1 | CHW Pump 1 | HW Pump 1 | HW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | HW Pump 1 | Boiler Pump 1
JSON_PATH:pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping | [13 empty] | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  | Chiller Loop 1 | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1
JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control | [13 empty] | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED
JSON_PATH:pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W
JSON_PATH:pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
JSON_PATH:pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
JSON_PATH:pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
JSON_PATH:pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
JSON_PATH:pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id | [17 empty] | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 |  |  |  | Secondary CHW Pump |  | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1
JSON_PATH:pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping | [17 empty] | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 |  |  |  | Secondary CHW Loop 1 |  | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1
JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control | [17 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  | VARIABLE_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED
JSON_PATH:pumps[1] | design_electric_power |  |  | Pump | Pump 2 | ASHRAE229 1 | design_electric_power | electric_power | W
JSON_PATH:pumps[1] | design_flow |  |  | Pump | Pump 2 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id | [17 empty] | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump | [6 empty] | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump
JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping | [17 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [6 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1
JSON_PATH:pumps[2] | speed_control |  |  | Pump | Pump 3 | ASHRAE229 1 | speed_control | [17 empty] | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED | [6 empty] | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED
JSON_PATH:fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  |  | Purchased CHW Loop 1 | Purchased HW Loop 1 | Purchased CHW Loop 1 |  | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  | Chiller Loop 1 | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1
JSON_PATH:fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type |  |  |  | HEATING | HEATING | HEATING | HEATING |  |  | COOLING | HEATING | COOLING |  | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING |  | HEATING |  | COOLING | COOLING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 1 | id | [28 empty] | Secondary CHW Loop 1
JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 1 | type | [28 empty] | COOLING
JSON_PATH:fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id |  |  |  |  | Purchased CHW Loop 1 |  | Purchased CHW Loop 1 |  |  |  |  | Purchased HW Loop 1 | [5 empty] | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | [5 empty] | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1
JSON_PATH:fluid_loops[1] | type |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | type |  |  |  |  | COOLING |  | COOLING |  |  |  |  | HEATING | [5 empty] | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | [5 empty] | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING
JSON_PATH:fluid_loops[1] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 2 | id | [17 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [6 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1
JSON_PATH:fluid_loops[1] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 2 | type | [17 empty] | COOLING |  | COOLING |  | COOLING |  | COOLING | [6 empty] | COOLING |  | COOLING |  | COOLING |  | COOLING

## TCDs
key1 | key2 | key3 | key4 | key5 | key6 | data_group | object_id | parent_id | data_element | unit_type | units | rule-19-1-a | rule-19-1-b | rule-19-1-c | rule-19-1-d | rule-19-1-e | rule-19-2-a | rule-19-2-b | rule-19-4-a | rule-19-4-b | rule-19-4-c | rule-19-4-d | rule-19-5-a | rule-19-5-b | rule-19-5-c | rule-19-5-d | rule-19-6-a | rule-19-6-b | rule-19-6-c | rule-19-6-d | rule-19-7-a | rule-19-7-b | rule-19-7-c | rule-19-7-d | rule-19-7-e | rule-19-7-f | rule-19-7-g | rule-19-7-h | rule-19-7-i | rule-19-7-j | rule-19-7-k | rule-19-8-a | rule-19-8-b | rule-19-9-a | rule-19-9-b | rule-19-9-c | rule-19-10-a | rule-19-10-b | rule-19-10-c | rule-19-10-d | rule-19-10-e | rule-19-10-f | rule-19-10-g | rule-19-10-h | rule-19-10-i | rule-19-11-a | rule-19-11-b | rule-19-11-c | rule-19-12-a | rule-19-12-b | rule-19-12-c | rule-19-12-d | rule-19-12-e | rule-19-13-a | rule-19-13-b | rule-19-13-c | rule-19-13-d | rule-19-13-e | rule-19-14-a | rule-19-14-b | rule-19-14-c | rule-19-14-d | rule-19-14-e | rule-19-14-f | rule-19-15-a | rule-19-15-b | rule-19-15-c | rule-19-15-d | rule-19-15-e | rule-19-16-a | rule-19-16-b | rule-19-16-c | rule-19-17-a | rule-19-17-a2 | rule-19-17-b | rule-19-19-a | rule-19-19-b | rule-19-19-c | rule-19-19-d | rule-19-20-a | rule-19-20-b | rule-19-21-a | rule-19-21-b | rule-19-21-c | rule-19-21-d | rule-19-21-e | rule-19-21-f | rule-19-21-g | rule-19-21-h | rule-19-21-i | rule-19-21-j | rule-19-21-k | rule-19-22-a | rule-19-22-b | rule-19-24-a | rule-19-24-b | rule-19-24-c | rule-19-24-d | rule-19-25-a | rule-19-25-b | rule-19-25-c | rule-19-25-d | rule-19-26-a | rule-19-26-b | rule-19-27-a | rule-19-27-b | rule-19-28-a | rule-19-28-b | rule-19-29-a | rule-19-29-b | rule-19-30-a | rule-19-30-b | rule-19-30-c | rule-19-31-a | rule-19-31-b | rule-19-32-a | rule-19-32-b | rule-19-35-a | rule-19-35-b | rule-19-35-c | rule-19-35-d | rule-19-36-a | rule-19-36-b
Section | [11 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
Rule | [11 empty] | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 17 | 17 | 17 | 19 | 19 | 19 | 19 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 26 | 26 | 27 | 27 | 28 | 28 | 29 | 29 | 30 | 30 | 30 | 31 | 31 | 32 | 32 | 35 | 35 | 35 | 35 | 36 | 36
Test | [11 empty] | a | b | c | d | e | a | b | a | b | c | d | a | b | c | d | a | b | c | d | a | b | c | d | e | f | g | h | i | j | k | a | b | a | b | c | a | b | c | d | e | f | g | h | i | a | b | c | a | b | c | d | e | a | b | c | d | e | a | b | c | d | e | f | a | b | c | d | e | a | b | c | a | a2 | b | a | b | c | d | a | b | a | b | c | d | e | f | g | h | i | j | k | a | b | a | b | c | d | a | b | c | d | a | b | a | b | a | b | a | b | a | b | c | a | b | a | b | a | b | c | d | a | b
Notes
test_description | [11 empty] | System 3 correctly utilizes autosized furnace with 25% oversizing and autosized DX coil with 15% oversizing | Airside HVAC has no cooling coil. It correctly utilizes an autosized furnace with 25% oversizing. Cooling side oversizing is not applicable | Airside HVAC has no heating coil. It correctly utilizes an autosized DX coil with 15% oversizing. Heating side oversizing is not applicable | System 3 incorrectly utilizes autosized furnace with no oversizing and autosized DX coil with no oversizing | Airside HVAC has no cooling coil. This RMD falls into NOT APPLICABLE case since it has OTHER heating system type. | System 7a with is_sized_using_coincident_load set to true. | System 7a with is_sized_using_coincident_load set to false. | testing | testing | testing | testing | System 3 with coincident_unmet_load_hours less than 300 hrs. | System 3 with the sum of unmet_load_hours_heating and unmet_load_hours_cooling less than 300 hrs. | System 3 with coincident_unmet_load_hours greater than 300 hrs. | System 3 with unmet_load_hours_cooling greater than 600 hrs. | System 3 with coincident_unmet_load_hours less than 300 hrs. | System 3 with the sum of unmet_load_hours_heating and unmet_load_hours_cooling less than 300 hrs. | System 3 with coincident_unmet_load_hours greater than 300 hrs. | System 3 with unmet_load_hours_cooling greater than 600 hrs. | System 7 serving two zones that do not have laboratory spaces where baseline and proposed OA are identical. (Case 1) | System 7 serving two zones, one has a laboratory space and one is not defined, baseline and proposed OA are identical. (Case 2) | System 6 serving two zones, all space types are undefined, baseline and proposed OA are identical (Case 3) | System 6 serving two zones that do not have laboratory spaces, one zone has DCV controls, baseline OA is greater than proposed OA (Case 4) | System 6 serving two zones, one has a laboratory space and one is not defined, one zone has DCV controls, baseline OA is greater than proposed OA (Case 5) | System 7 serving two zones, one has a laboratory space and one does not have a laboratory space, one zone has air distribution effectiveness greater than 1, baseline OA is greater than proposed OA (Case 6) | System 7 serving two zones, one has a laboratory space and one is not defined, one zone has air distribution effectiveness greater than 1, baseline OA is greater than proposed OA (Case 7) | System 7 serving two zones, baseline OA is less than proposed OA (Case 8) | System 7 serving two zones that do not have laboratory spaces, baseline OA is greater than proposed OA (Case 9) | System 7 serving two zones where the baseline and proposed minimum outside air is equal, but the outside airflow multiplier schedule is not identical (Case 10) | System 7 serving two zones, one zone has a laboratory space and one zone is not defined, baseline OA is greater than proposed OA (Case 11) | System 3 with CO2_ZONE ventilation control type, 3500 minimum outdoor airflows, and 150 occupants in the 1000 ft2 zone | System 3 with NONE ventilation control type, 2800 minimum outdoor airflows, and 20 occupants in the 1000 ft2 zone | System 9 without air economizer. | System 9 with FIXED_FRACTION air economizer. | System 9 with ENTHALPY air economizer. | CZ 5A, System 11, w/ Economizer, economizer in the proposed - PASS (Case 5) | CZ 5A, System 5, w/o Economizer, economizer in the proposed - FAIL (Case 7) | CZ 5A, System 3, primarily serving computer room, w/o Economizer, no economizer in the proposed - PASS (Case 1) | CZ 5A, System 3, primarily serving computer room, w Economizer, no economizer in the proposed - FAIL (Case 3) | CZ 5A, System 5, w/o Economizer, no economizer in the proposed - FAIL (Case 6) | CZ 3A, System 5, w/o Economizer, no economizer in the proposed - NOT APPLICABLE (NA Climate Zone) | CZ 5A, System 9, w/o Economizer, no economizer in the proposed - NOT APPLICABLE (NA System Type) | CZ 5A, System 5, w/o Economizer, building has refrigerated cases, building type is retail, no economizer in the proposed - UNDETERMINED (Case 2) | CZ 5A, System 5, w/ Economizer, building has refrigerated cases, building type is retail, no economizer in the proposed - UNDETERMINED (Case 4) | Baseline building with computer room utilizese baseline System 11. The system includes an integrated fluid economizer | Baseline building with computer room does not utilize baseline System 11. Therefore this building does not apply | Baseline building with computer room utilizese baseline System 11. The system does not include an integrated fluid economizer | System 9 with TEMPERATURE based air economizer and 75F high limit shutoff temp. | System 9 with TEMPERATURE based air economizer and 100F high limit shutoff temp. | System 9 with ENTHALPY based air economizer and 75F high limit shutoff temp. | System 9 without air economizer setup. | System 9 with wrong climate zone setup. | Baseline system type 7, supply-air-to-room temperature set-point difference of 20F, required ventilation or makeup air does not exceed. Airflow rate is correctly sized from temperature difference. | Baseline system type 11, serving lab space, supply-air-to-room temperature set-point difference of 17F, required ventilation or makeup air does not exceed. Airflow rate is correctly sized from temperature difference. | Baseline system type 7, supply-air-to-room temperature set-point difference of 20F, required ventilation exceeds sizing based on temperature difference. Airflow rate incorrectly based on temperature difference instead of required ventilation. | Baseline system type 11, serving lab space, supply-air-to-room temperature set-point difference of 20F, required ventilation or makeup air does not exceed sizing. Airflow rate is sized from the incorrect temperature difference. | Baseline system type 7, supply-air-to-room temperature set-point difference of 15F. The sum of zone terminal primary airflow from zones served by the system is identical to the corresponding sum of terminal primary flow in the proposed model. | System 11, no return or relief in the proposed, no return or relief cfm in the baseline - PASS | System 11, no return or relief in the proposed, return fan cfm modeled in the baseline - FAIL | System 5, return fan in the proposed, baseline supply 1000 cfm, minimum OA 200 cfm, return sized correctly at 900 cfm - PASS | System 5, return fan in the proposed, baseline supply 1000 cfm, minimum OA 50 cfm, return sized correctly at 950 cfm - PASS | System 5, return fan in the proposed, baseline supply 1000 cfm, minimum OA 200 cfm, return sized incorrectly at 800 cfm - FAIL | System 5, multiple return fans modeled - UNDETERMINED | Baseline system type 10, minimum ventilation does not exceed auto-sized airflow rates. Supply airflow rates are correctly based on the temperature difference between 105F and the design space-heating temperature set point. | Baseline system type 10, minimum ventilation does not exceed auto-sized airflow rates. Supply airflow rates are incorrectly based on a supply-air-to-room temperature set-point difference of 20F. | Baseline system type 9, minimum ventilation exceeds the auto-sized airflow rates. Supply airflow rates are correctly based on the minimum ventilation airflow rates. | Baseline system type 9, minimum ventilation exceeds the auto-sized airflow rates. Supply airflow rates are incorrectly based on the temperature difference between 105F and the design space-heating temperature set point. | Baseline system type 9 with more than one supply fan. | Proposed system type 9 includes a fan to provide non-mechanical cooling. The baseline system design has a separate fan to provide nonmechanical cooling sized and controlled the same as proposed case. This results in an undetermined per 19-16 | Proposed system type 10 includes a fan to provide non-mechanical cooling. The baseline system design has a separate fan to provide nonmechanical cooling sized and controlled the same as proposed case. This results in an undetermined per 19-16 |  | System 1 with `SIMPLE` specification method for supply/return/exhaust/relief fans and each of the 5 fans has 59 W design electric power for a total of 295 W with 1000 cfm design supply airflow. | System 1 with `SIMPLE` specification method for supply/return/exhaust/relief fans and each of the 5 fans has 56 W design electric power for a total of 280 W with 1000 cfm design supply airflow. | For baseline system 1 and 2, the total fan electrical power (Pfan) for supply, return, exhaust, and relief shall be = CFMs × 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm | System 9 with `SIMPLE` specification method for supply/return/exhaust/relief fans and each of 5 fans have 59 W design electric power for a total of 295 W with 1000 cfm design supply airflow. | System 10 with `SIMPLE` specification method for supply/return/exhaust/relief fans and each fans have 80 W design electric power with 800 cfm design supply airflow. | There is more than one supply fan in the baseline HVAC system | There is non-mechanical cooling associated with the zone served by the baseline HVAC system in the proposed model | Project contains baseline system 7 with 'SIMPLE' specification method for supply/return/relief/exhaust fans. Proposed supply/return/relief/exhaust fans have 100W/50W/0W/50W design electric power respectively. Baseline fan power is proportionally distributed according to the proposed fan power. | Project contains baseline system 5 with 'SIMPLE' specification method for supply/return/relief/exhaust fans. Proposed supply/return/relief/exhaust fans have 100W/50W/0W/50W design electric power respectively. Baseline fan power is not proportionally distributed according to the proposed fan power. | Case 1: Project is in climate zone 5A and contains baseline system 7 with 5000 cfm of supply air and 75% OA. Energy recovery is correctly modeled for the system. | Case 2: Project is in climate zone 5A and contains baseline system 7 with 5000 cfm of supply air and 75% OA. System serves spaces that are not cooled and that are heated to less than 60F. Energy recovery is not modeled for the system. | Case 3: Project is in climate zone 5A and contains baseline system 5 with 5000 cfm of supply air and 75% OA. System serves zones likely to be exhausting toxic, flammable, or corrosive fumes or paint or dust that do not have energy recovery for the proposed system. | Case 4: Project is in climate zone 3A and contains baseline system 10 with heating only, 5000 cfm of supply air, and 75% OA. System serves zones that do not have energy recovery for the proposed system. | Case 5:Project is in climate zone 5A and contains baseline system 5 with 5000 cfm of supply air and 75% OA. The largest exhaust source is less than 75% of the design outdoor airflow. | Case 6:Project is in climate zone 5A and contains baseline system 5 with 5000 cfm of supply air and 75% OA. The proposed system has dehumidification that employs energy recovery in series with the cooling coil. | Case 8:Project is in climate zone 5A and contains baseline system 3 with 5000 cfm of supply air and 75% OA. System serves a kitchen type space indicating that exception 3 may be applicable. | Case 9:Project is in climate zone 5A and contains baseline system 5 with 5000 cfm of supply air and 75% OA. The proposed HVAC system contains more than one exhaust fan, and the largest exhaust source could be less than 75% of the design outdoor airflow, but it cannot be determined if exception 6 is applicable. | Case 10:Project is in climate zone 5A and contains baseline system 7 with 5000 cfm of supply air and 69% OA. Energy recovery is correctly not modeled for the system. | Case 11:Project is in climate zone 5A and contains baseline system 7 with 5000 cfm of supply air and 75% OA. Energy recovery is incorrectly not modeled for the system and not all space types have been defined so applicability of exceptions 2 and 3 cannot be determined. | Case 12: Project is in climate zone 5A and contains baseline system 7 with 5000 cfm of supply air and 75% OA. Energy recovery is incorrectly not modeled for the system. | Baseline system type 11 correctly modeled with "WHEN MINIMUM OUTSIDE AIR" energy recovery operations to allow bypass for economizer control. | Baseline system type 11 incorrectly modeled with "WHEN FANS ON" energy recovery operations, preventing bypass for economizer control. | Project consists of a single-zone HW/CHW VAV HVAC system with a minimum outdoor airflow requirement of 100 cfm. The HVAC fan system correctly operates continuously during occupied hours. | Project consists of a single-zone HW/CHW VAV HVAC system with a minimum outdoor airflow requirement of 100 cfm. The HVAC fan system incorrectly cycles on and off during occupied hours to maintain temperature setpoints, but not outdoor airflow requirements. | Project consists of a packaged single-zone HVAC system with no minimum outdoor airflow requirement. The HVAC fan system correctly cycles on and off during occupied hours to maintain temperature setpoints. | Project consists of a packaged single-zone HVAC system with no minimum outdoor airflow requirement. The HVAC fan system is set to remain off during occupied hours. Under the current rule definition, this is a failed outcome. | Project contains baseline system 11 with a minimum outdoor airflow requirement of 100 cfm. The HVAC fan system correctly operates continuously during occupied hours. | Project contains baseline system 11 with a minimum outdoor airflow requirement of 100 cfm. The HVAC fan system incorrectly cycles on and off during occupied hours to maintain temperature setpoints, but not outdoor airflow requirements. | Project contains baseline system 7 with no minimum outdoor airflow requirement. The HVAC fan system correctly cycles on and off during occupied hours to maintain temperature setpoints. | Project contains baseline system 3 with no minimum outdoor airflow requirement. The HVAC fan system is set to remain off during occupied hours. Under the current rule definition, this is a failed outcome. | Project consists of a HW/CHW VAV HVAC system serving a healthcare facility operating room with 100 CFM minimum OA requirement. Fan system is correctly set to CONTINUOUS operation during unoccupied hours. | Project consists of a single-zone HW/CHW VAV HVAC system serving an animal health facility room with 100 CFM minimum OA requirement. Fan system is incorrectly set to KEEP OFF during unoccupied hours. | Project consists of a baseline System 7 serving a healthcare facility operating room with 100 CFM minimum OA requirement. Fan system is correctly set to CONTINUOUS operation during unoccupied hours. | Project consists of a baseline System 11 serving an animal health facility room with 100 CFM minimum OA requirement. Fan system is incorrectly set to KEEP OFF during unoccupied hours. | Project does not have spaces with health and safety mandated minimum ventilation requirements. HVAC fans correctly cycle on and off to maintain temperature setpoint during unoccupied hours. | Project does not have spaces with health and safety mandated minimum ventilation requirements. HVAC fans incorrectly stay off during unoccupied hours. | Project does not have spaces with health and safety mandated minimum ventilation requirements. HVAC fans correctly cycle on and off to maintain temperature setpoint during unoccupied hours. | Project does not have spaces with health and safety mandated minimum ventilation requirements. HVAC fans incorrectly stay off during unoccupied hours. | Baseline HVAC system is System 6 and requires a manual check to see that the terminal-unit fan and reheat coil are being energized to meet the heating set point during occupied hours | Baseline HVAC system is System 8 and requires a manual check to see that the terminal-unit fan and reheat coil are being energized to meet the heating set point during occupied hours | Baseline HVAC system does not have an air loop and this rule does not apply | Project contains a computer room served by a packaged terminal heat pump system. HVAC fans correctly operate continuously during unoccupied hours. | Project contains a computer room served by a packaged terminal heat pump system. HVAC fans correctly operate continuously during unoccupied hours. | Project contains a computer room served by a baseline system 2. HVAC fans correctly operate continuously during unoccupied hours. | Project contains a computer room served by a baseline system 2. HVAC fans incorrectly cycle on and off during unoccupied hours. | Project is in climate zone 5A and contains system 7 with 2 zones. All spaces served by the system are defined as lab. 5,000 cfm of aggregated minimum OA flow for the baseline system, and 4,000 cfm in the proposed. | Project is in climate zone 4A and contains system 7 with 2 zones. The only defined space type for spaces served by the system is lab, but not all space types are defined. 5,000 cfm of aggregated minimum OA flow for the baseline system, and 4,000 cfm in the proposed. | Project is in climate zone 5A and contains system 5 with 2 zones. None of the spaces served by the system have space types defined. 5,000 cfm of aggregated minimum OA flow for the baseline system, and 4,000 cfm in the proposed. | Project is in climate zone 4A and contains system 5 with 2 zones. There are spaces served by the system with non-lab space types defined. 5,000 cfm of aggregated minimum OA flow for the baseline system, and 4,000 cfm in the proposed. | Baseline system 7 with air capacity > 5,000 CFM and a minimum supply air ratio greater than 70% has an ERV greater than 50% enthalpy recovery ratio | Baseline system 7 did not have ERV
expected_rule_outcome | [11 empty] | pass | pass | pass | fail | not_applicable | pass | fail | pass | fail | not_applicable | undetermined | pass | pass | fail | fail | pass | pass | fail | fail | pass | pass | pass | fail | fail | undetermined | undetermined | undetermined | fail | fail | fail | pass | fail | pass | pass | fail | pass | fail | pass | fail | fail | not_applicable | not_applicable | undetermined | undetermined | undetermined | not_applicable | undetermined | pass | fail | fail | not_applicable | not_applicable | pass | pass | fail | fail | undetermined | pass | fail | pass | pass | fail | undetermined | pass | fail | pass | fail | undetermined | undetermined | undetermined | not_applicable | pass | pass | fail | pass | fail | undetermined | undetermined | pass | fail | pass | pass | pass | pass | pass | pass | undetermined | undetermined | pass | fail | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | undetermined | undetermined | not_applicable | pass | fail | pass | fail | undetermined | undetermined | undetermined | not_applicable | undetermined | not_applicable
standard | rule_id | [10 empty] | 19-1 | 19-1 | 19-1 | 19-1 | 19-1 | 19-2 | 19-2 | 19-4 | 19-4 | 19-4 | 19-4 | 19-5 | 19-5 | 19-5 | 19-5 | 19-6 | 19-6 | 19-6 | 19-6 | 19-7 | 19-7 | 19-7 | 19-7 | 19-7 | 19-7 | 19-7 | 19-7 | 19-7 | 19-7 | 19-7 | 19-8 | 19-8 | 19-9 | 19-9 | 19-9 | 19-10 | 19-10 | 19-10 | 19-10 | 19-10 | 19-10 | 19-10 | 19-10 | 19-10 | 19-11 | 19-11 | 19-11 | 19-12 | 19-12 | 19-12 | 19-12 | 19-12 | 19-13 | 19-13 | 19-13 | 19-13 | 19-13 | 19-14 | 19-14 | 19-14 | 19-14 | 19-14 | 19-14 | 19-15 | 19-15 | 19-15 | 19-15 | 19-15 | 19-16 | 19-16 | 19-16 | 19-17 | 19-17 | 19-17 | 19-19 | 19-19 | 19-19 | 19-19 | 19-20 | 19-20 | 19-21 | 19-21 | 19-21 | 19-21 | 19-21 | 19-21 | 19-21 | 19-21 | 19-21 | 19-21 | 19-21 | 19-22 | 19-22 | 19-24 | 19-24 | 19-24 | 19-24 | 19-25 | 19-25 | 19-25 | 19-25 | 19-26 | 19-26 | 19-27 | 19-27 | 19-28 | 19-28 | 19-29 | 19-29 | 19-30 | 19-30 | 19-30 | 19-31 | 19-31 | 19-32 | 19-32 | 19-35 | 19-35 | 19-35 | 19-35 | 19-36 | 19-36
standard | ruleset_reference | [10 empty] | G3.1.2.2 | G3.1.2.2 | G3.1.2.2 | G3.1.2.2 | G3.1.2.2 | G3.1.2.2 | G3.1.2.2 | G3.1.2.2.1 | G3.1.2.2.1 | G3.1.2.2.1 | G3.1.2.2.1 | G3.1.2.3 | G3.1.2.3 | G3.1.2.3 | G3.1.2.3 | G3.1.2.3 | G3.1.2.3 | G3.1.2.3 | G3.1.2.3 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 and Exception 2 | G3.1.2.5 Exception #1 | G3.1.2.5 Exception #1 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6 | G3.1.2.6.1 | G3.1.2.6.1 | G3.1.2.6.1 | G3.1.2.7 | G3.1.2.7 | G3.1.2.7 | G3.1.2.7 | G3.1.2.7 | G3.1.2.8.1 and Exception 1 | G3.1.2.8.1 and Exception 1 | G3.1.2.8.1 and Exception 1 | G3.1.2.8.1 and Exception 1 | G3.1.2.8.1 and Exception 1 | G3.1.2.8.1 | G3.1.2.8.1 | G3.1.2.8.1 | G3.1.2.8.1 | G3.1.2.8.1 | G3.1.2.8.1 | G3.1.2.8.2 | G3.1.2.8.2 | G3.1.2.8.2 | G3.1.2.8.2 | G3.1.2.8.2 | G3.1.2.8.2 | G3.1.2.8.2 | G3.1.2.8.2 | G3.1.2.9 | G3.1.2.9 | G3.1.2.9 | G3.1.2.9 | G3.1.2.9 | G3.1.2.9 | G3.1.2.9 | G3.1.2.9 | G3.1.2.9 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | G3.1.2.10 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Table G3.1 Section 4 & G3.1.2.4 | Section G3.1.2.4 Exception #1 | Section G3.1.2.4 Exception #1 | Section G3.1.2.4 Exception #1 | Table G3.1 Section 4 Exception #3 | Table G3.1 Section 4 Exception #3 | Table G3.1 Section 4 Exception #3 | Table G3.1 Section 4 Exception #3 | G3.1.2.5 Exception #4 | G3.1.2.5 Exception #4 | G3.1.2.5 Exception #4 | G3.1.2.5 Exception #4 | G3.1.2.10 | G3.1.2.10
standard | rule_description | [10 empty] | HVAC system coil capacities for the baseline building design shall be oversized by 15% for cooling and 25% for heating. | HVAC system coil capacities for the baseline building design shall be oversized by 15% for cooling and 25% for heating. | HVAC system coil capacities for the baseline building design shall be oversized by 15% for cooling and 25% for heating. | HVAC system coil capacities for the baseline building design shall be oversized by 15% for cooling and 25% for heating. | HVAC system coil capacities for the baseline building design shall be oversized by 15% for cooling and 25% for heating. | Baseline building plant capacities shall be based on coincident loads. | Baseline building plant capacities shall be based on coincident loads. | For baseline cooling sizing runs in residential dwelling units, the infiltration, occupants, lighting, gas and electricity using equipment hourly schedule shall be the same as the most used hourly weekday schedule from the annual simulation. | For baseline cooling sizing runs in residential dwelling units, the infiltration, occupants, lighting, gas and electricity using equipment hourly schedule shall be the same as the most used hourly weekday schedule from the annual simulation. | For baseline cooling sizing runs in residential dwelling units, the infiltration, occupants, lighting, gas and electricity using equipment hourly schedule shall be the same as the most used hourly weekday schedule from the annual simulation. | For baseline cooling sizing runs in residential dwelling units, the infiltration, occupants, lighting, gas and electricity using equipment hourly schedule shall be the same as the most used hourly weekday schedule from the annual simulation. | Unmet load hours for the proposed design shall not exceed 300 (of the 8760 hours simulated). | Unmet load hours for the proposed design shall not exceed 300 (of the 8760 hours simulated). | Unmet load hours for the proposed design shall not exceed 300 (of the 8760 hours simulated). | Unmet load hours for the proposed design shall not exceed 300 (of the 8760 hours simulated). | Unmet load hours for the baseline design shall not exceed 300 (of the 8760 hours simulated). | Unmet load hours for the baseline design shall not exceed 300 (of the 8760 hours simulated). | Unmet load hours for the baseline design shall not exceed 300 (of the 8760 hours simulated). | Unmet load hours for the baseline design shall not exceed 300 (of the 8760 hours simulated). | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Minimum ventilation system outdoor air intake flow shall be the same for the proposed design and baseline building design except when any of the 4 exceptions defined in Section G3.1.2.5 are met. Exceptions 2. When designing systems in accordance with Standard 62.1, Section 6.2, “Ventilation Rate Procedure,” reduced ventilation airflow rates may be calculated for each HVAC zone in the proposed design with a zone air distribution effectiveness (Ez) > 1.0 as defined by Standard 62.1, Table 6-2. Baseline ventilation airflow rates in those zones shall be calcu-lated using the proposed design Ventilation Rate Procedure calculation with the following change only. Zone air distribution effectiveness shall be changed to (Ez) = 1.0 in each zone having a zone air distribution effectiveness (Ez) > 1.0. Proposed design and baseline build-ing design Ventilation Rate Procedure calculations, as described in Standard 62.1, shall be submitted to the rating authority to claim credit for this exception. | Demand control ventilation is modeled in the baseline design in systems with outdoor air capacity greater than 3000 cfm serving areas with an average occupant design capacity greater than 100 people per 1000 ft^2. | Demand control ventilation is modeled in the baseline design in systems with outdoor air capacity greater than 3000 cfm serving areas with an average occupant design capacity greater than 100 people per 1000 ft^2. | Air economizers shall not be included in baseline HVAC Systems 1, 2, 9, and 10. | Air economizers shall not be included in baseline HVAC Systems 1, 2, 9, and 10. | Air economizers shall not be included in baseline HVAC Systems 1, 2, 9, and 10. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | Air economizers shall be included in baseline HVAC Systems 3 through 8, and 11, 12, and 13 based on climate as specified in Table G3.1.2.6. Exceptions: 1. Systems that include gas-phase air cleaning to meet the requirements of Standard 62.1, Section 6.1.2. This exception shall be used only if the system in the proposed design does not match the building design. 2. Where the use of outdoor air for cooling will affect supermarket open refrigerated case-work systems. This exception shall only be used if the system in the proposed design does not use an economizer. If the exception is used, an economizer shall not be included in the baseline building design. 3. Systems that serve computer rooms complying with Section G3.1.2.6.1. | For systems that serve computer rooms, if the baseline system is HVAC System 11, it shall include an integrated fluid economizer meeting the requirements of Section 6.5.1.2 in the baseline building design. | For systems that serve computer rooms, if the baseline system is HVAC System 11, it shall include an integrated fluid economizer meeting the requirements of Section 6.5.1.2 in the baseline building design. | For systems that serve computer rooms, if the baseline system is HVAC System 11, it shall include an integrated fluid economizer meeting the requirements of Section 6.5.1.2 in the baseline building design. | The baseline system economizer high-limit shutoff shall be a dry-bulb fixed switch with set-point temperatures in accordance with the values in Table G3.1.2.7. | The baseline system economizer high-limit shutoff shall be a dry-bulb fixed switch with set-point temperatures in accordance with the values in Table G3.1.2.7. | The baseline system economizer high-limit shutoff shall be a dry-bulb fixed switch with set-point temperatures in accordance with the values in Table G3.1.2.7. | The baseline system economizer high-limit shutoff shall be a dry-bulb fixed switch with set-point temperatures in accordance with the values in Table G3.1.2.7. | The baseline system economizer high-limit shutoff shall be a dry-bulb fixed switch with set-point temperatures in accordance with the values in Table G3.1.2.7. | For baseline system types 1-8 and 11-13, system design supply airflow rates shall be based on a supply-air-to-room temperature set-point difference of 20°F or the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. For systems with multiple zone thermostat setpoints, use the design set point that will result in the lowest supply air cooling set point or highest supply air heating set point. Exceptions: 1. For baseline systems serving laboratory spaces, airflow rate shall be based on a supply-air-to-room temperature set-point difference of 17°F or the required ventilation air or makeup air, whichever is greater. | For baseline system types 1-8 and 11-13, system design supply airflow rates shall be based on a supply-air-to-room temperature set-point difference of 20°F or the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. For systems with multiple zone thermostat setpoints, use the design set point that will result in the lowest supply air cooling set point or highest supply air heating set point. Exceptions: 1. For baseline systems serving laboratory spaces, airflow rate shall be based on a supply-air-to-room temperature set-point difference of 17°F or the required ventilation air or makeup air, whichever is greater. | For baseline system types 1-8 and 11-13, system design supply airflow rates shall be based on a supply-air-to-room temperature set-point difference of 20°F or the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. For systems with multiple zone thermostat setpoints, use the design set point that will result in the lowest supply air cooling set point or highest supply air heating set point. Exceptions: 1. For baseline systems serving laboratory spaces, airflow rate shall be based on a supply-air-to-room temperature set-point difference of 17°F or the required ventilation air or makeup air, whichever is greater. | For baseline system types 1-8 and 11-13, system design supply airflow rates shall be based on a supply-air-to-room temperature set-point difference of 20°F or the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. For systems with multiple zone thermostat setpoints, use the design set point that will result in the lowest supply air cooling set point or highest supply air heating set point. Exceptions: 1. For baseline systems serving laboratory spaces, airflow rate shall be based on a supply-air-to-room temperature set-point difference of 17°F or the required ventilation air or makeup air, whichever is greater. | For baseline system types 1-8 and 11-13, system design supply airflow rates shall be based on a supply-air-to-room temperature set-point difference of 20°F or the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. For systems with multiple zone thermostat setpoints, use the design set point that will result in the lowest supply air cooling set point or highest supply air heating set point. Exceptions: 1. For baseline systems serving laboratory spaces, airflow rate shall be based on a supply-air-to-room temperature set-point difference of 17°F or the required ventilation air or makeup air, whichever is greater. | For baseline system types 1-8 and 11-13, if return or relief fans are specified in the proposed design, the baseline building design shall also be modeled with fans serving the same functions and sized for the baseline system supply fan air quantity less the minimum outdoor air, or 90% of the supply fan air quantity, whichever is larger. | For baseline system types 1-8 and 11-13, if return or relief fans are specified in the proposed design, the baseline building design shall also be modeled with fans serving the same functions and sized for the baseline system supply fan air quantity less the minimum outdoor air, or 90% of the supply fan air quantity, whichever is larger. | For baseline system types 1-8 and 11-13, if return or relief fans are specified in the proposed design, the baseline building design shall also be modeled with fans serving the same functions and sized for the baseline system supply fan air quantity less the minimum outdoor air, or 90% of the supply fan air quantity, whichever is larger. | For baseline system types 1-8 and 11-13, if return or relief fans are specified in the proposed design, the baseline building design shall also be modeled with fans serving the same functions and sized for the baseline system supply fan air quantity less the minimum outdoor air, or 90% of the supply fan air quantity, whichever is larger. | For baseline system types 1-8 and 11-13, if return or relief fans are specified in the proposed design, the baseline building design shall also be modeled with fans serving the same functions and sized for the baseline system supply fan air quantity less the minimum outdoor air, or 90% of the supply fan air quantity, whichever is larger. | For baseline system types 1-8 and 11-13, if return or relief fans are specified in the proposed design, the baseline building design shall also be modeled with fans serving the same functions and sized for the baseline system supply fan air quantity less the minimum outdoor air, or 90% of the supply fan air quantity, whichever is larger. | For baseline system types 9 & 10, the system design supply airflow rates shall be based on the temperature difference between a supply air temperature set point of 105°F and the design space-heating temperature set point, the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. | For baseline system types 9 & 10, the system design supply airflow rates shall be based on the temperature difference between a supply air temperature set point of 105°F and the design space-heating temperature set point, the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. | For baseline system types 9 & 10, the system design supply airflow rates shall be based on the temperature difference between a supply air temperature set point of 105°F and the design space-heating temperature set point, the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. | For baseline system types 9 & 10, the system design supply airflow rates shall be based on the temperature difference between a supply air temperature set point of 105°F and the design space-heating temperature set point, the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. | For baseline system types 9 & 10, the system design supply airflow rates shall be based on the temperature difference between a supply air temperature set point of 105°F and the design space-heating temperature set point, the minimum outdoor airflow rate, or the airflow rate required to comply with applicable codes or accreditation standards, whichever is greater. | For zones served by baseline system types 9 & 10, if the proposed design includes a fan or fans sized and controlled to provide non-mechanical cooling, the baseline building design shall include a separate fan to provide nonmechanical cooling, sized and controlled the same as the proposed design. | For zones served by baseline system types 9 & 10, if the proposed design includes a fan or fans sized and controlled to provide non-mechanical cooling, the baseline building design shall include a separate fan to provide nonmechanical cooling, sized and controlled the same as the proposed design. | For zones served by baseline system types 9 & 10, if the proposed design includes a fan or fans sized and controlled to provide non-mechanical cooling, the baseline building design shall include a separate fan to provide nonmechanical cooling, sized and controlled the same as the proposed design. | For baseline system 1 and 2, the total fan electrical power (Pfan) for supply, return, exhaust, and relief shall be = CFMs x 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm | For baseline system 1 and 2, the total fan electrical power (Pfan) for supply, return, exhaust, and relief shall be = CFMs x 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm | For baseline system 1 and 2, the total fan electrical power (Pfan) for supply, return, exhaust, and relief shall be = CFMs x 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm | For baseline systems 9 and 10 the system fan electrical power (Pfan) for supply, return, exhaust, and relief shall be CFMs × 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm. If modeling a non-mechanical cooling fan is required by Section G3.1.2.8.2, there is a fan power allowance of Pfan = CFMnmc × 0.054, where, CFMnmc = the baseline non-mechanical cooling fan airflow, cfm for the non-mechanical cooling. | For baseline systems 9 and 10 the system fan electrical power (Pfan) for supply, return, exhaust, and relief shall be CFMs × 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm. If modeling a non-mechanical cooling fan is required by Section G3.1.2.8.2, there is a fan power allowance of Pfan = CFMnmc × 0.054, where, CFMnmc = the baseline non-mechanical cooling fan airflow, cfm for the non-mechanical cooling. | For baseline systems 9 and 10 the system fan electrical power (Pfan) for supply, return, exhaust, and relief shall be CFMs × 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm. If modeling a non-mechanical cooling fan is required by Section G3.1.2.8.2, there is a fan power allowance of Pfan = CFMnmc × 0.054, where, CFMnmc = the baseline non-mechanical cooling fan airflow, cfm for the non-mechanical cooling. | For baseline systems 9 and 10 the system fan electrical power (Pfan) for supply, return, exhaust, and relief shall be CFMs × 0.3, where, CFMs = the baseline system maximum design supply fan airflow rate, cfm. If modeling a non-mechanical cooling fan is required by Section G3.1.2.8.2, there is a fan power allowance of Pfan = CFMnmc × 0.054, where, CFMnmc = the baseline non-mechanical cooling fan airflow, cfm for the non-mechanical cooling. | The calculated system fan power shall be distributed to supply, return, exhaust, and relief fans in the same proportion as the proposed design. | The calculated system fan power shall be distributed to supply, return, exhaust, and relief fans in the same proportion as the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems with >= 5,000 CFM supply air and >= 70 %OA shall have energy recovery with 50% enthalpy recovery ratio. Exceptions include: 1. Systems serving spaces that are not cooled and that are heated to less than 60°F. 2. Systems exhausting toxic, flammable, or corrosive fumes or paint or dust. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 3. Commercial kitchen hoods (grease) classified as Type 1 by NFPA 96. This exception shall only be used if exhaust air energy recovery is not used in the proposed design. 4. Heating systems in Climate Zones 0 through 3. 5. Cooling systems in Climate Zones 3C, 4C, 5B, 5C, 6B, 7, and 8. 6. Where the largest exhaust source is less than 75% of the design outdoor airflow. This excep-tion shall only be used if exhaust air energy recovery is not used in the proposed design. 7. Systems requiring dehumidification that employ energy recovery in series with the cooling coil. This exception shall only be used if exhaust air energy recovery and series-style energy recovery coils are not used in the proposed design. | Baseline systems modeled with exhaust air energy recovery shall allow bypass for economizer control where applicable. | Baseline systems modeled with exhaust air energy recovery shall allow bypass for economizer control where applicable. | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the proposed design. | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the proposed design. | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the proposed design. | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the proposed design. | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the baseline design. | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the baseline design. | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the baseline design. | Schedules for HVAC fans that provide outdoor air for ventilation shall run continuously whenever spaces are occupied in the baseline design. | HVAC fans shall remain on during unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements during unoccupied hours in the proposed design. | HVAC fans shall remain on during unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements during unoccupied hours in the proposed design. | HVAC fans shall remain on during unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements during unoccupied hours in the baseline design. | HVAC fans shall remain on during unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements during unoccupied hours in the baseline design. | Schedules for HVAC fans that provide outdoor air for ventilation excluding unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements shall be cycled ON and OFF to meet heating and cooling loads during unoccupied hours in the proposed design. | Schedules for HVAC fans that provide outdoor air for ventilation excluding unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements shall be cycled ON and OFF to meet heating and cooling loads during unoccupied hours in the proposed design. | Schedules for HVAC fans that provide outdoor air for ventilation excluding unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements shall be cycled ON and OFF to meet heating and cooling loads during unoccupied hours in the baseline design. | Schedules for HVAC fans that provide outdoor air for ventilation excluding unoccupied hours in spaces that have health and safety mandated minimum ventilation requirements shall be cycled ON and OFF to meet heating and cooling loads during unoccupied hours in the baseline design. | For Systems 6 and 8, only the terminal-unit fan and reheat coil shall be energized to meet heating set point during unoccupied hours in the baseline design. | For Systems 6 and 8, only the terminal-unit fan and reheat coil shall be energized to meet heating set point during unoccupied hours in the baseline design. | For Systems 6 and 8, only the terminal-unit fan and reheat coil shall be energized to meet heating set point during unoccupied hours in the baseline design. | HVAC fans shall remain on during unoccupied hours in systems primarily serving computer rooms in the proposed design. | HVAC fans shall remain on during unoccupied hours in systems primarily serving computer rooms in the proposed design. | HVAC fans shall remain on during unoccupied hours in systems primarily serving computer rooms in the baseline design. | HVAC fans shall remain on during unoccupied hours in systems primarily serving computer rooms in the baseline design. | For baseline systems serving only laboratory spaces that are prohibited from recirculating return air by code or accreditation standards, the baseline system shall be modeled as 100% outdoor air. Rule only applies when baseline outdoor air CFM is modeled as greater than proposed design outdoor air CFM. | For baseline systems serving only laboratory spaces that are prohibited from recirculating return air by code or accreditation standards, the baseline system shall be modeled as 100% outdoor air. Rule only applies when baseline outdoor air CFM is modeled as greater than proposed design outdoor air CFM. | For baseline systems serving only laboratory spaces that are prohibited from recirculating return air by code or accreditation standards, the baseline system shall be modeled as 100% outdoor air. Rule only applies when baseline outdoor air CFM is modeled as greater than proposed design outdoor air CFM. | For baseline systems serving only laboratory spaces that are prohibited from recirculating return air by code or accreditation standards, the baseline system shall be modeled as 100% outdoor air. Rule only applies when baseline outdoor air CFM is modeled as greater than proposed design outdoor air CFM. | Baseline systems required to model energy recovery per G3.1.2.10 shall be modeled with a 50% enthalpy recovery ratio. | Baseline systems required to model energy recovery per G3.1.2.10 shall be modeled with a 50% enthalpy recovery ratio.
standard | applicable_rmr | [10 empty] | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Proposed RMR | Proposed RMR | Proposed RMR | Proposed RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Proposed RMR | Proposed RMR | Proposed RMR | Proposed RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Proposed RMR | Proposed RMR | Baseline RMR | Baseline RMR | Proposed RMR | Proposed RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Proposed RMR | Proposed RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR
standard | rule_assertion | [10 empty] | = | = | = | = | = | = | = | = | = | = | = | <= | <= | <= | <= | <= | <= | <= | <= | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | = | =
standard | comparison_value | [10 empty] | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value
standard | primary_rule | [10 empty] | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Applicability | Applicability | Applicability | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Applicability | Applicability | Applicability | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Full | Applicability | Applicability | Applicability | Full | Full | Full | Full | Applicability | Applicability | Applicability | Applicability | Applicability | Applicability
standard | schema_version | [10 empty] | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29 | 0.0.29
template_lookup | [11 empty] | System_3_PSZ_AC_Gas_Furnace | Generic Airside | Generic Airside | System_3_PSZ_AC_Gas_Furnace | Generic Airside | System_7a_VAV_HW_Reheat | System_7a_VAV_HW_Reheat | 19_4_template_system_7a | 19_4_template_system_7a | 19_4_template_system_7a | 19_4_template_system_7a | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_6_PVAV_Elec_Reheat | System_6_PVAV_Elec_Reheat | System_6_PVAV_Elec_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_11.1_VAV_SZ | System_5_PVAV_HW_Reheat | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_5_PVAV_HW_Reheat | System_9_Warm_Air_Furnace_Gas | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_11.1_VAV_SZ | System_1_PTAC | System_11.1_VAV_SZ | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_7_VAV_HW_Reheat | System_11.1_VAV_SZ | System_7_VAV_HW_Reheat | System_11.1_VAV_SZ | System_7_VAV_HW_Reheat | System_11.1a_VAV_SZ | System_11.1a_VAV_SZ | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_10_Heating_Resistance_Elec | System_10_Heating_Resistance_Elec | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_9_Warm_Air_Furnace_Gas | System_10_Heating_Resistance_Elec | System_1_PTAC | System_1_PTAC | System_1_PTAC | System_1_PTAC | System_9_Warm_Air_Furnace_Gas | System_10_Heating_Resistance_Elec | System_10_Heating_Resistance_Elec | System_10_Heating_Resistance_Elec | System_7_VAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_7_VAV_HW_Reheat | System_9_Warm_Air_Furnace_Gas | System_5_PVAV_HW_Reheat | System_10_Heating_Resistance_Elec | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_3_PSZ_AC_Gas_Furnace | System_5_PVAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_11.1_VAV_SZ | System_11.1_VAV_SZ | System_11.2_VAV_SZ | System_11.2_VAV_SZ | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_3_PSZ_AC_Gas_Furnace | System_3_PSZ_AC_Gas_Furnace | System_7_VAV_HW_Reheat | System_11.2_VAV_SZ | System_7_VAV_HW_Reheat | System_11.2_VAV_SZ | System_2_PTHP | System_7_VAV_HW_Reheat | System_2_PTHP | System_7_VAV_HW_Reheat | System_6_PVAV_Elec_Reheat | System_8_PFP_Reheat | System_1_PTAC | System_2_PTHP | System_2_PTHP | System_2_PTHP | System_2_PTHP | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat
rmr_template | user | [107 empty] | true | true | true | true
rmr_template | proposed | [21 empty] | true | true | true | true |  |  |  |  | true | true | true | true | true | true | true | true | true | true | true | [5 empty] | true | true | true | true | true | true | true | true | true | [8 empty] | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true |  |  |  | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true |  |  | true | true | true | true | true | true | true | true | true | true |  |  | true | true | [5 empty] | true | true |  |  | true | true | true | true | true | true
rmr_template | baseline | [10 empty] | true | true | true | true | true | true | true | true | true | true | true |  |  |  |  | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true |  |  |  |  | true | true | true | true |  |  | true | true |  |  | true | true | true | true | true |  |  | true | true | true | true | true | true | true | true
rmr_template | json_template | id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
rmr_template | json_template | weather | climate_zone |  |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone
rmr_template | json_template | calendar | day_of_week_for_january_1 |  |  | ASHRAE229 | ASHRAE229 1 | calendar | day_of_week_for_january_1 | [9 empty] | SUNDAY | SUNDAY | SUNDAY | SUNDAY
rmr_template | json_template | ruleset_model_descriptions[0] | id |  |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1
rmr_template | json_template | JSON_PATH:buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1
rmr_template | json_template | JSON_PATH:buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
rmr_template | json_template | JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
rmr_template | json_template | JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 |  |  | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 |  |  | Required Heating Schedule 1 |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | PTAC Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | Air Terminal | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | VAV Air Terminal 1 | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | PTHP Terminal 1 | VAV Air Terminal 1 | PTHP Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | PTAC Terminal 1 | PTHP Terminal 1 | PTHP Terminal 1 | PTHP Terminal 1 | PTHP Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | false | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | false | false | false | false | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | false | true | false | true | true | true | false | false | false | false | false | true | true | true | true | true | true
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_systems |  |  | System Type 3 | Airside System 1 | Airside System 1 | System Type 3 | Airside System 1 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System 7 | System 7 | System 6 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System Type 3 | System Type 3 | System 9 | System 9 | System 9 | System 11 | System 5 | System Type 3 | System Type 3 | System Type 3 | System 5 | System 9 | System 5 | System 5 | System 11 | PTAC 1 | System 11 | System 9 | System 9 | System 9 | System 9 | System 9 | System 7 | System 11 | System 7 | System 11 | System 7 | System 11 | System 11 | System 5 | System 5 | System 5 | System 5 | System 10 | System 10 | System 9 | System 9 | System 9 | System 9 | System 10 | PTAC 1 | PTAC 1 | PTAC 1 | PTAC 1 | System 9 | System 10 | System 10 | System 10 | System 7 | System 5 | System 7 | System 9 | System 5 | System 10 | System 5 | System 5 | System Type 3 | System 5 | System 7 | System 7 | System 7 | System 11 | System 11 | System 11 | System 11 | System Type 3 | System Type 3 | System 7 | System 7 | System Type 3 | System Type 3 | System 7 | System 11 | System 7 | System 11 | PTHP 1 | System 7 | PTHP 1 | System 7 | System 6 | System 8 | PTAC 1 | PTHP 1 | PTHP 1 | PTHP 1 | PTHP 1 | System 7 | System 7 | System 5 | System 5 | System 7 | System 7
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source | [7 empty] | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | [8 empty] | HOT_WATER | HOT_WATER | ELECTRIC | ELECTRIC | ELECTRIC | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | [6 empty] | HOT_WATER |  |  |  | HOT_WATER |  | HOT_WATER | HOT_WATER | [8 empty] | HOT_WATER |  | HOT_WATER |  | HOT_WATER |  |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | ELECTRIC | ELECTRIC |  |  |  |  | ELECTRIC | [5 empty] | ELECTRIC | ELECTRIC | ELECTRIC | HOT_WATER | HOT_WATER | HOT_WATER |  | HOT_WATER | ELECTRIC | HOT_WATER | HOT_WATER |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | [6 empty] | HOT_WATER | HOT_WATER |  |  | HOT_WATER |  | HOT_WATER |  |  | HOT_WATER |  | HOT_WATER | ELECTRIC | ELECTRIC | [5 empty] | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [6 empty] | Boiler Loop 1 |  |  |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [15 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [6 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 |  | Boiler Loop 1 |  |  | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | [5 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_source |  | Air Terminal | Terminal 1 | Zone 1 | cooling_source
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | cooling_from_loop
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan | id | Air Terminal | Terminal 1 | Zone 1 | fan | [23 empty] | Fan 1 | Fan 1 | Fan 1 | [39 empty] | Terminal Fan 1 | Terminal Fan 1 |  |  |  |  | Terminal Fan 1 | [5 empty] | Terminal Fan 1 | Terminal Fan 1 | Terminal Fan 1 | [5 empty] | Terminal Fan 1 | [25 empty] | Fan 1 | Fan 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 1 | Zone 1 | fan_configuration | [23 empty] | PARALLEL | PARALLEL | PARALLEL | [85 empty] | PARALLEL | PARALLEL
rmr_template | json_template | JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id | [7 empty] | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | [8 empty] | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | [6 empty] | Thermal Zone 2 |  |  |  | Thermal Zone 2 |  | Thermal Zone 2 | Thermal Zone 2 | [8 empty] | Thermal Zone 2 |  | Thermal Zone 2 |  | Thermal Zone 2 |  |  | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | [15 empty] | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 |  | Thermal Zone 2 |  | Thermal Zone 2 | Thermal Zone 2 |  | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | [6 empty] | Thermal Zone 2 | Thermal Zone 2 |  |  | Thermal Zone 2 |  | Thermal Zone 2 |  |  | Thermal Zone 2 |  | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | [5 empty] | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule | [7 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [8 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [6 empty] | Required Cooling Schedule 1 |  |  |  | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [8 empty] | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [15 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [6 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 |  |  | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 |  |  | Required Cooling Schedule 1 |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [5 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule | [7 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | [8 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | [6 empty] | Required Heating Schedule 1 |  |  |  | Required Heating Schedule 1 |  | Required Heating Schedule 1 | Required Heating Schedule 1 | [8 empty] | Required Heating Schedule 1 |  | Required Heating Schedule 1 |  | Required Heating Schedule 1 |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | [15 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 |  | Required Heating Schedule 1 |  | Required Heating Schedule 1 | Required Heating Schedule 1 |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | [6 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 |  |  | Required Heating Schedule 1 |  | Required Heating Schedule 1 |  |  | Required Heating Schedule 1 |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | [5 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id | [7 empty] | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | [8 empty] | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | [6 empty] | VAV Air Terminal 2 |  |  |  | VAV Air Terminal 2 |  | VAV Air Terminal 2 | VAV Air Terminal 2 | [8 empty] | VAV Air Terminal 2 |  | VAV Air Terminal 2 |  | VAV Air Terminal 2 |  |  | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | [15 empty] | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 |  | VAV Air Terminal 2 |  | VAV Air Terminal 2 | VAV Air Terminal 2 |  | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | [6 empty] | VAV Air Terminal 2 | VAV Air Terminal 2 |  |  | VAV Air Terminal 2 |  | VAV Air Terminal 2 |  |  | VAV Air Terminal 2 |  | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | [5 empty] | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration | [7 empty] | true | true | true | true | true | true | [8 empty] | TRUE | TRUE | true | true | true | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | [6 empty] | true |  |  |  | true |  | true | true | [8 empty] | TRUE |  | TRUE |  | TRUE |  |  | true | true | true | true | [15 empty] | TRUE | true | TRUE |  | true |  | true | true |  | true | TRUE | TRUE | TRUE | [6 empty] | TRUE | TRUE |  |  | TRUE |  | TRUE |  |  | TRUE |  | TRUE | true | true | [5 empty] | TRUE | TRUE | true | true | TRUE | TRUE
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type | [7 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [8 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [6 empty] | VARIABLE_AIR_VOLUME |  |  |  | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [8 empty] | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME |  |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [15 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [6 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME |  |  | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME |  |  | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [5 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_systems | [7 empty] | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | [8 empty] | System 7 | System 7 | System 6 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | [6 empty] | System 5 |  |  |  | System 5 |  | System 5 | System 5 | [8 empty] | System 7 |  | System 7 |  | System 7 |  |  | System 5 | System 5 | System 5 | System 5 | [15 empty] | System 7 | System 5 | System 7 |  | System 5 |  | System 5 | System 5 |  | System 5 | System 7 | System 7 | System 7 | [6 empty] | System 7 | System 7 |  |  | System 7 |  | System 7 |  |  | System 7 |  | System 7 | System 6 | System 8 | [5 empty] | System 7 | System 7 | System 5 | System 5 | System 7 | System 7
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source | [7 empty] | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | [8 empty] | HOT_WATER | HOT_WATER | ELECTRIC | ELECTRIC | ELECTRIC | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | [6 empty] | HOT_WATER |  |  |  | HOT_WATER |  | HOT_WATER | HOT_WATER | [8 empty] | HOT_WATER |  | HOT_WATER |  | HOT_WATER |  |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | [15 empty] | HOT_WATER | HOT_WATER | HOT_WATER |  | HOT_WATER |  | HOT_WATER | HOT_WATER |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | [6 empty] | HOT_WATER | HOT_WATER |  |  | HOT_WATER |  | HOT_WATER |  |  | HOT_WATER |  | HOT_WATER | ELECTRIC | ELECTRIC | [5 empty] | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [6 empty] | Boiler Loop 1 |  |  |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [15 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [6 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 |  | Boiler Loop 1 |  |  | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | [5 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | cooling_source |  | Air Terminal | Terminal 2 | Zone 2 | cooling_source
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | cooling_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | cooling_from_loop
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan | id | Air Terminal | Terminal 2 | Zone 2 | fan | [23 empty] | Fan 2 | Fan 2 | Fan 2 | [85 empty] | Fan 2 | Fan 2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration | [23 empty] | PARALLEL | PARALLEL | PARALLEL | [85 empty] | PARALLEL | PARALLEL
rmr_template | json_template | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | System Type 3 | Airside System 1 | Airside System 1 | System Type 3 | Airside System 1 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System 7 | System 7 | System 6 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System Type 3 | System Type 3 | System 9 | System 9 | System 9 | System 11 | System 5 | System Type 3 | System Type 3 | System Type 3 | System 5 | System 9 | System 5 | System 5 | System 11 | PTAC 1 | System 11 | System 9 | System 9 | System 9 | System 9 | System 9 | System 7 | System 11 | System 7 | System 11 | System 7 | System 11 | System 11 | System 5 | System 5 | System 5 | System 5 | System 10 | System 10 | System 9 | System 9 | System 9 | System 9 | System 10 | PTAC 1 | PTAC 1 | PTAC 1 | PTAC 1 | System 9 | System 10 | System 10 | System 10 | System 7 | System 5 | System 7 | System 9 | System 5 | System 10 | System 5 | System 5 | System Type 3 | System 5 | System 7 | System 7 | System 7 | System 11 | System 11 | System 11 | System 11 | System Type 3 | System Type 3 | System 7 | System 7 | System Type 3 | System Type 3 | System 7 | System 11 | System 7 | System 11 | PTHP 1 | System 7 | PTHP 1 | System 7 | System 6 | System 8 | PTAC 1 | PTHP 1 | PTHP 1 | PTHP 1 | PTHP 1 | System 7 | System 7 | System 5 | System 5 | System 7 | System 7
rmr_template | json_template | JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | DX Coil 1 | Cooling System 1 | Cooling System 1 | DX Coil 1 | Cooling System 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 |  |  |  | CHW Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 |  | DX Coil 1 | DX Coil 1 | CHW Coil 1 | DX Coil 1 | CHW Coil 1 | [5 empty] | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | [7 empty] | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 |  |  |  |  | CHW Coil 1 | DX Coil 1 | CHW Coil 1 |  | DX Coil 1 |  | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | HP Cooling Coil 1 | CHW Coil 1 | HP Cooling Coil 1 | CHW Coil 1 | DX Coil 1 | CHW Coil 1 | DX Coil 1 | HP Cooling Coil 1 | HP Cooling Coil 1 | HP Cooling Coil 1 | HP Cooling Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1
rmr_template | json_template | JSON_PATH:cooling_system | type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | DIRECT_EXPANSION |  |  | DIRECT_EXPANSION |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION |  |  |  | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION |  | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | [5 empty] | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | [7 empty] | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION |  |  |  |  | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP |  | DIRECT_EXPANSION |  | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP
rmr_template | json_template | JSON_PATH:cooling_system | chilled_water_loop |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop | [7 empty] | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | [8 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | [5 empty] | Secondary CHW Loop 1 | [8 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [5 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | [19 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [7 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [5 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  | Furnace Coil 1 | Heating System 1 | Heating System 1 | Furnace Coil 1 | Heating System 1 | [6 empty] | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | [11 empty] | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Heating Coil 1 |  | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 |  | Furnace Coil 1 |  |  | Heating Coil 1 | HHW Coil 1 | Heating Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 |  | Heating Coil 1 |  | Heating Coil 1 |  | Heating Coil 1 | Heating Coil 1 |  |  |  |  | Heating Coil 1 | Heating Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Heating Coil 1 | HHW Coil 1 | HHW Coil 1 | HHW Coil 1 | HHW Coil 1 | Furnace Coil 1 | Heating Coil 1 | Heating Coil 1 | Heating Coil 1 |  |  |  | Furnace Coil 1 |  | Heating Coil 1 |  |  | Furnace Coil 1 |  |  |  |  | Heating Coil 1 | Heating Coil 1 | Boiler Coil 1 | Boiler Coil 1 | Furnace Coil 1 | Furnace Coil 1 |  |  | Furnace Coil 1 | Furnace Coil 1 |  | Boiler Coil 1 |  | Boiler Coil 1 | HP Heating Coil 1 |  | HP Heating Coil 1 |  |  |  | HHW Coil 1 | HP Heating Coil 1 | HP Heating Coil 1 | HP Heating Coil 1 | HP Heating Coil 1
rmr_template | json_template | JSON_PATH:heating_system | type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  | FURNACE |  |  | FURNACE | [7 empty] | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE | [11 empty] | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE | ELECTRIC_RESISTANCE |  | FURNACE | FURNACE | FURNACE |  | FURNACE |  |  | ELECTRIC_RESISTANCE | FLUID_LOOP | ELECTRIC_RESISTANCE | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE |  | ELECTRIC_RESISTANCE |  | ELECTRIC_RESISTANCE |  | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE |  |  |  |  | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE | FURNACE | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FURNACE | FURNACE | FURNACE | FURNACE |  |  |  | FURNACE |  | FURNACE |  |  | FURNACE |  |  |  |  | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | FURNACE | FURNACE |  |  | FURNACE | FURNACE |  | FLUID_LOOP |  | FLUID_LOOP | HEAT_PUMP |  | HEAT_PUMP |  |  |  | FLUID_LOOP | HEAT_PUMP | HEAT_PUMP | HEAT_PUMP | HEAT_PUMP
rmr_template | json_template | JSON_PATH:heating_system | energy_source_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type | [34 empty] | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | [6 empty] | NATURAL_GAS | [5 empty] | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | [11 empty] | ELECTRICITY | ELECTRICITY | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | ELECTRICITY |  |  |  |  | NATURAL_GAS | ELECTRICITY | ELECTRICITY | ELECTRICITY |  |  |  | NATURAL_GAS |  | ELECTRICITY
rmr_template | json_template | JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop | [47 empty] | Boiler Loop 1 | [24 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [19 empty] | Boiler Loop 1 | Boiler Loop 1 | [7 empty] | Boiler Loop 1 |  | Boiler Loop 1 | [6 empty] | Boiler Loop 1
rmr_template | json_template | JSON_PATH:preheat_system | id |  |  | PreheatSystem | Heating System 1 | HVAC 1 | id | [7 empty] | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | [8 empty] | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | [6 empty] | Preheat Coil 1 |  |  |  | Preheat Coil 1 |  | Preheat Coil 1 | Preheat Coil 1 | [8 empty] | Preheat Coil 1 |  | Preheat Coil 1 |  | Preheat Coil 1 |  |  | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | [15 empty] | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 |  | Preheat Coil 1 |  | Preheat Coil 1 | Preheat Coil 1 |  | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | [6 empty] | Preheat Coil 1 | Preheat Coil 1 |  |  | Preheat Coil 1 |  | Preheat Coil 1 |  |  | Preheat Coil 1 |  | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | [5 empty] | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1
rmr_template | json_template | JSON_PATH:preheat_system | type |  |  | PreheatSystem | Heating System 1 | HVAC 1 | heating_system_type | [7 empty] | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | [8 empty] | FLUID_LOOP | FLUID_LOOP | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | [6 empty] | FLUID_LOOP |  |  |  | FLUID_LOOP |  | FLUID_LOOP | FLUID_LOOP | [8 empty] | FLUID_LOOP |  | FLUID_LOOP |  | FLUID_LOOP |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | [15 empty] | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP |  | FLUID_LOOP |  | FLUID_LOOP | FLUID_LOOP |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | [6 empty] | FLUID_LOOP | FLUID_LOOP |  |  | FLUID_LOOP |  | FLUID_LOOP |  |  | FLUID_LOOP |  | FLUID_LOOP | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE | [5 empty] | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP
rmr_template | json_template | JSON_PATH:preheat_system | hot_water_loop |  |  | PreheatSystem | Heating System 2 | HVAC 1 | hot_water_loop | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [6 empty] | Boiler Loop 1 |  |  |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [15 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [6 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 |  | Boiler Loop 1 |  |  | Boiler Loop 1 |  | Boiler Loop 1 | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | CAV Fan System 1 | Fan System 1 | Fan System 1 | CAV Fan System 1 | Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1
rmr_template | json_template | JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | CONSTANT |  |  | CONSTANT |  | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE
rmr_template | json_template | JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1
rmr_template | json_template | JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  |  |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  | Return Fan 1 |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | [5 empty] | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1
rmr_template | json_template | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id | [7 empty] | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | [8 empty] | Boiler 1 | Boiler 1 |  |  |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | [6 empty] | Boiler 1 |  |  |  | Boiler 1 |  | Boiler 1 | Boiler 1 |  | Boiler 1 | [6 empty] | Boiler 1 |  | Boiler 1 |  | Boiler 1 |  |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | [7 empty] | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  |  |  |  | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 |  | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  |  | Boiler 1 | Boiler 1 |  |  | Boiler 1 | Boiler 1 |  |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 |  | Boiler 1 |  | Boiler 1 | Boiler 1 |  |  |  |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1
rmr_template | json_template | JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [6 empty] | Boiler Loop 1 |  |  |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | [6 empty] | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type | [7 empty] | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | [8 empty] | NATURAL_GAS | NATURAL_GAS |  |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | [6 empty] | NATURAL_GAS |  |  |  | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | [6 empty] | NATURAL_GAS |  | NATURAL_GAS |  | NATURAL_GAS |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | [7 empty] | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  |  |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  |  | NATURAL_GAS | NATURAL_GAS |  |  | NATURAL_GAS | NATURAL_GAS |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS |  | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS |  |  |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS
rmr_template | json_template | JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id | [21 empty] | Chiller 1 | Chiller 1 |  |  |  | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | [5 empty] | Chiller 1 | [8 empty] | Chiller 1 |  | Chiller 1 | [5 empty] | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | [21 empty] | Chiller 1 |  | Chiller 1 | [7 empty] | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 |  |  | Chiller 1 | Chiller 1 |  |  | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  | Chiller 1 | [5 empty] | Chiller 1 | Chiller 1 |  |  | Chiller 1 | Chiller 1
rmr_template | json_template | JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop | [21 empty] | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | [5 empty] | Chiller Loop 1 | [8 empty] | Chiller Loop 1 |  | Chiller Loop 1 | [5 empty] | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | [21 empty] | Chiller Loop 1 |  | Chiller Loop 1 | [7 empty] | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 | [5 empty] | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1
rmr_template | json_template | JSON_PATH:chillers[0] | design_capacity |  |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[0] | energy_source_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type
rmr_template | json_template | JSON_PATH:chillers[0] | full_load_efficiency |  |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton
rmr_template | json_template | JSON_PATH:chillers[0] | compressor_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type
rmr_template | json_template | JSON_PATH:chillers[1] | id |  |  | Chiller | Chiller 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[1] | cooling_loop |  |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[1] | design_capacity |  |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[2] | id |  |  | Chiller | Chiller 3 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[2] | cooling_loop |  |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[2] | design_capacity |  |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[3] | id |  |  | Chiller | Chiller 4 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[3] | cooling_loop |  |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[3] | design_capacity |  |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:external_fluid_sources[0] | id |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | id | [7 empty] | Purchased CW 1 | Purchased CW 1 | Purchased CW 1 | Purchased CW 1 | Purchased CW 1 | Purchased CW 1 | [46 empty] | Purchased CW 1 | Purchased CW 1
rmr_template | json_template | JSON_PATH:external_fluid_sources[0] | loop |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | loop | [7 empty] | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | [46 empty] | Chilled Water Loop 1 | Chilled Water Loop 1
rmr_template | json_template | JSON_PATH:external_fluid_sources[0] | type |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | type | [7 empty] | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | [46 empty] | CHILLED_WATER | CHILLED_WATER
rmr_template | json_template | JSON_PATH:external_fluid_sources[1] | id |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:external_fluid_sources[1] | loop |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:external_fluid_sources[1] | type |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:heat_rejections[0] | id |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:heat_rejections[0] | loop |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:heat_rejections[0] | type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_water_flowrate |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
rmr_template | json_template | JSON_PATH:heat_rejections[0] | fan_speed_control |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control
rmr_template | json_template | JSON_PATH:heat_rejections[0] | range |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature_difference | R
rmr_template | json_template | JSON_PATH:heat_rejections[0] | reset_type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type
rmr_template | json_template | JSON_PATH:heat_rejections[1] | id |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:heat_rejections[1] | loop |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:heat_rejections[1] | type |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id | [7 empty] | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | [8 empty] | Boiler Pump 1 | Boiler Pump 1 |  |  |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | [5 empty] | Chiller Pump 1 | Boiler Pump 1 |  |  |  | Boiler Pump 1 |  | Boiler Pump 1 | Boiler Pump 1 | Chiller Pump 1 |  | Chiller Pump 1 | [5 empty] | Boiler Pump 1 | Chiller Pump 1 | Boiler Pump 1 | Chiller Pump 1 | Boiler Pump 1 | CHW Pump 1 | CHW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | [15 empty] | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1 |  | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  |  | Boiler Pump 1 | Boiler Pump 1 |  |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1 |  | Boiler Pump 1 |  | Boiler Pump 1 | [5 empty] | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1
rmr_template | json_template | JSON_PATH:pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [5 empty] | Chiller Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 | [5 empty] | Boiler Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [15 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | [5 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control | [7 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | [8 empty] | FIXED_SPEED | FIXED_SPEED |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | [5 empty] | FIXED_SPEED | FIXED_SPEED |  |  |  | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | [5 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | [15 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED |  | FIXED_SPEED |  | FIXED_SPEED | [5 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED
rmr_template | json_template | JSON_PATH:pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W
rmr_template | json_template | JSON_PATH:pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
rmr_template | json_template | JSON_PATH:pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
rmr_template | json_template | JSON_PATH:pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
rmr_template | json_template | JSON_PATH:pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id | [7 empty] | CHW Pump 1 | CHW Pump 1 | CHW Pump 1 | CHW Pump 1 | CHW Pump 1 | CHW Pump 1 | [8 empty] | Chiller Pump 1 | Chiller Pump 1 |  |  |  | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | [5 empty] | Secondary CHW Pump | [8 empty] | Secondary CHW Pump |  | Secondary CHW Pump | [5 empty] | Chiller Pump 1 | Secondary CHW Pump | Chiller Pump 1 | Secondary CHW Pump | Chiller Pump 1 | [21 empty] | Chiller Pump 1 |  | Chiller Pump 1 | [7 empty] | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Secondary CHW Pump | Secondary CHW Pump | Chiller Pump 1 | Chiller Pump 1 |  |  | Chiller Pump 1 | Chiller Pump 1 |  |  | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 |  | Chiller Pump 1 |  | Chiller Pump 1 |  | Chiller Pump 1 | [5 empty] | Chiller Pump 1 | Chiller Pump 1 |  |  | Chiller Pump 1 | Chiller Pump 1
rmr_template | json_template | JSON_PATH:pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping | [7 empty] | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | [8 empty] | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | [5 empty] | Secondary CHW Loop 1 | [8 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [5 empty] | Chiller Loop 1 | Secondary CHW Loop 1 | Chiller Loop 1 | Secondary CHW Loop 1 | Chiller Loop 1 | [21 empty] | Chiller Loop 1 |  | Chiller Loop 1 | [7 empty] | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 | [5 empty] | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1
rmr_template | json_template | JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control | [7 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | [8 empty] | FIXED_SPEED | FIXED_SPEED |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | [5 empty] | VARIABLE_SPEED | [8 empty] | VARIABLE_SPEED |  | VARIABLE_SPEED | [5 empty] | FIXED_SPEED | VARIABLE_SPEED | FIXED_SPEED | VARIABLE_SPEED | FIXED_SPEED | [21 empty] | FIXED_SPEED |  | FIXED_SPEED | [7 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | FIXED_SPEED | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED |  | FIXED_SPEED |  | FIXED_SPEED | [5 empty] | FIXED_SPEED | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED
rmr_template | json_template | JSON_PATH:pumps[1] | design_electric_power |  |  | Pump | Pump 2 | ASHRAE229 1 | design_electric_power | electric_power | W
rmr_template | json_template | JSON_PATH:pumps[1] | design_flow |  |  | Pump | Pump 2 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id | [21 empty] | Secondary CHW Pump | Secondary CHW Pump |  |  |  | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump | [22 empty] | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump | [21 empty] | Secondary CHW Pump |  | Secondary CHW Pump | [7 empty] | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump |  |  | Secondary CHW Pump | Secondary CHW Pump |  |  | Secondary CHW Pump | Secondary CHW Pump |  |  | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump | [5 empty] | Secondary CHW Pump | Secondary CHW Pump |  |  | Secondary CHW Pump | Secondary CHW Pump
rmr_template | json_template | JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping | [21 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | [22 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [21 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [7 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [5 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:pumps[2] | speed_control |  |  | Pump | Pump 3 | ASHRAE229 1 | speed_control | [21 empty] | VARIABLE_SPEED | VARIABLE_SPEED |  |  |  | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | [22 empty] | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED | [21 empty] | VARIABLE_SPEED |  | VARIABLE_SPEED | [7 empty] | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED |  |  | VARIABLE_SPEED | VARIABLE_SPEED |  |  | VARIABLE_SPEED | VARIABLE_SPEED |  |  | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED | [5 empty] | VARIABLE_SPEED | VARIABLE_SPEED |  |  | VARIABLE_SPEED | VARIABLE_SPEED
rmr_template | json_template | JSON_PATH:fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [5 empty] | Chiller Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Chiller Loop 1 | [5 empty] | Boiler Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [7 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type | [7 empty] | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | [8 empty] | HEATING | HEATING |  |  |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | [5 empty] | COOLING | HEATING |  |  |  | HEATING |  | HEATING | HEATING | COOLING | HEATING | COOLING | [5 empty] | HEATING | COOLING | HEATING | COOLING | HEATING | COOLING | COOLING | HEATING | HEATING | HEATING | HEATING | [7 empty] | HEATING | HEATING | HEATING | HEATING |  |  |  |  | HEATING | HEATING | HEATING |  | HEATING |  | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | COOLING | COOLING | HEATING | HEATING |  |  | HEATING | HEATING |  |  | HEATING | HEATING | HEATING | HEATING |  | HEATING |  | HEATING |  | HEATING | HEATING |  |  |  |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
rmr_template | json_template | JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 1 | id | [37 empty] | Secondary CHW Loop 1 | [8 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [6 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [35 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 1 | type | [37 empty] | COOLING | [8 empty] | COOLING |  | COOLING | [6 empty] | COOLING |  | COOLING | [35 empty] | COOLING | COOLING
rmr_template | json_template | JSON_PATH:fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id | [7 empty] | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | [8 empty] | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | [22 empty] | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 | [21 empty] | Chiller Loop 1 |  | Chiller Loop 1 | [7 empty] | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 | [5 empty] | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[1] | type |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | type | [7 empty] | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | [8 empty] | COOLING | COOLING |  |  |  | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | [22 empty] | COOLING |  | COOLING |  | COOLING | [21 empty] | COOLING |  | COOLING | [7 empty] | COOLING | COOLING | COOLING |  |  | COOLING | COOLING |  |  | COOLING | COOLING |  |  | COOLING | COOLING | COOLING | COOLING |  | COOLING |  | COOLING |  | COOLING | [5 empty] | COOLING | COOLING |  |  | COOLING | COOLING
rmr_template | json_template | JSON_PATH:fluid_loops[1] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 2 | id | [21 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | [22 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [21 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [7 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [5 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[1] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 2 | type | [21 empty] | COOLING | COOLING |  |  |  | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | [22 empty] | COOLING |  | COOLING |  | COOLING | [21 empty] | COOLING |  | COOLING | [7 empty] | COOLING | COOLING | COOLING |  |  | COOLING | COOLING |  |  | COOLING | COOLING |  |  | COOLING | COOLING | COOLING | COOLING |  | COOLING |  | COOLING |  | COOLING | [5 empty] | COOLING | COOLING |  |  | COOLING | COOLING
rmr_transformations | user | id | [102 empty] | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
rmr_transformations | user | weather | climate_zone
rmr_transformations | user | ruleset_model_descriptions[0] | id | [101 empty] | RMD 1 | RMD 1 | RMD 1 | RMD 1
rmr_transformations | user | JSON_PATH:buildings[0] | id | [101 empty] | Building 1 | Building 1 | Building 1 | Building 1
rmr_transformations | user | JSON_PATH:buildings[0] | building_open_schedule | [101 empty] | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
rmr_transformations | user | JSON_PATH:buildings[0] | refrigerated_casess[0] | id
rmr_transformations | user | JSON_PATH:buildings[0] | refrigerated_casess[0] | type
rmr_transformations | user | JSON_PATH: building_segments[0] | id | [101 empty] | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
rmr_transformations | user | JSON_PATH:building_segments[0] | lighting_building_area_type
rmr_transformations | user | JSON_PATH:zones[0] | id | [101 empty] | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
rmr_transformations | user | JSON_PATH:zones[0] | design_thermostat_cooling_setpoint | [6 empty] | temperature | F
rmr_transformations | user | JSON_PATH:zones[0] | design_thermostat_heating_setpoint | [6 empty] | temperature | F
rmr_transformations | user | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule | [101 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
rmr_transformations | user | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule | [101 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
rmr_transformations | user | JSON_PATH:zones[0] | infiltration | id
rmr_transformations | user | JSON_PATH:zones[0] | infiltration | multiplier_schedule
rmr_transformations | user | JSON_PATH:zones[0] | zonal_exhaust_fan | id
rmr_transformations | user | JSON_PATH:zones[0] | zonal_exhaust_fan | specification_method
rmr_transformations | user | JSON_PATH:zones[0] | zonal_exhaust_fan | design_electric_power
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | id
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | number_of_occupants
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | floor_area | [5 empty] | area | ft2
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | lighting_space_type
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | ventilation_space_type
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | interior_lighting[0] | id
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | interior_lighting[0] | lighting_multiplier_schedule
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | miscellaneous_equipment[0] | id
rmr_transformations | user | JSON_PATH:zones[0] | spaces[0] | miscellaneous_equipment[0] | multiplier_schedule
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | id | [100 empty] | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted | [100 empty] | true | true | true | true
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | type | [100 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system | [100 empty] | System 11 | System 11 | System Type 3 | System Type 3
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | primary_airflow | [5 empty] | air_flow_rate | cfm
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | heating_source
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | heating_from_loop
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | cooling_source
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | fan | id
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | fan_configuration
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | supply_design_cooling_setpoint_temperature | [5 empty] | temperature | F
rmr_transformations | user | JSON_PATH:zones[0] | terminals[0] | supply_design_heating_setpoint_temperature | [5 empty] | temperature | F
rmr_transformations | user | JSON_PATH:zones[1] | id
rmr_transformations | user | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule
rmr_transformations | user | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule
rmr_transformations | user | JSON_PATH:zones[1] | spaces[0] | id
rmr_transformations | user | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule
rmr_transformations | user | JSON_PATH:zones[1] | spaces[0] | floor_area
rmr_transformations | user | JSON_PATH:zones[1] | spaces[0] | lighting_space_type
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | id
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | type
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | heating_source
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | heating_from_loop
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | cooling_source
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | cooling_from_loop
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | fan | id
rmr_transformations | user | JSON_PATH:zones[1] | terminals[0] | fan_configuration
rmr_transformations | user | JSON_PATH:zones[1] | infiltration | id
rmr_transformations | user | JSON_PATH:zones[1] | infiltration | multiplier_schedule
rmr_transformations | user | JSON_PATH:spaces[1] | id
rmr_transformations | user | JSON_PATH:spaces[1] | lighting_space_type
rmr_transformations | user | JSON_PATH:spaces[1] | ventilation_space_type
rmr_transformations | user | JSON_PATH:spaces[1] | occupant_multiplier_schedule
rmr_transformations | user | JSON_PATH:spaces[1] | interior_lighting[0] | id
rmr_transformations | user | JSON_PATH:spaces[1] | interior_lighting[0] | lighting_multiplier_schedule
rmr_transformations | user | JSON_PATH:spaces[1] | miscellaneous_equipment[0] | id
rmr_transformations | user | JSON_PATH:spaces[1] | miscellaneous_equipment[0] | multiplier_schedule
rmr_transformations | user | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id | [101 empty] | System 11 | System 11 | System Type 3 | System Type 3
rmr_transformations | user | JSON_PATH:cooling_system | id | [101 empty] | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1
rmr_transformations | user | JSON_PATH:cooling_system | type | [101 empty] | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION
rmr_transformations | user | JSON_PATH:cooling_system | is_autosized
rmr_transformations | user | JSON_PATH:cooling_system | oversizing_factor
rmr_transformations | user | JSON_PATH:cooling_system | chilled_water_loop | [101 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1
rmr_transformations | user | JSON_PATH:heating_system | id | [101 empty] | Boiler Coil 1 | Boiler Coil 1 | Furnace Coil 1 | Furnace Coil 1
rmr_transformations | user | JSON_PATH:heating_system | type | [101 empty] | FLUID_LOOP | FLUID_LOOP | FURNACE | FURNACE
rmr_transformations | user | JSON_PATH:heating_system | is_autosized
rmr_transformations | user | JSON_PATH:heating_system | oversizing_factor
rmr_transformations | user | JSON_PATH:heating_system | energy_source_type
rmr_transformations | user | JSON_PATH:heating_system | hot_water_loop
rmr_transformations | user | JSON_PATH:preheat_system | id | [101 empty] | Boiler Loop 1 | Boiler Loop 1
rmr_transformations | user | JSON_PATH:preheat_system | type
rmr_transformations | user | JSON_PATH:preheat_system | hot_water_loop
rmr_transformations | user | JSON_PATH:fan_system | id | [101 empty] | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1
rmr_transformations | user | JSON_PATH:fan_system | fan_control | [101 empty] | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT
rmr_transformations | user | JSON_PATH:fan_system | operation_during_occupied | [101 empty] | CONTINUOUS | CYCLING | CYCLING | KEEP_OFF | CONTINUOUS | CYCLING | CYCLING | KEEP_OFF
rmr_transformations | user | JSON_PATH:fan_system | operation_during_unoccupied
rmr_transformations | user | JSON_PATH:fan_system | minimum_outdoor_airflow | [6 empty] | air_flow_rate | cfm | [97 empty] | 100 | 100 | 0 | 0
rmr_transformations | user | JSON_PATH:fan_system | demand_control_ventilation_control
rmr_transformations | user | JSON_PATH:boilers[0] | id | [101 empty] | Boiler 1 | Boiler 1
rmr_transformations | user | JSON_PATH:boilers[0] | loop | [101 empty] | Boiler Loop 1 | Boiler Loop 1
rmr_transformations | user | JSON_PATH:boilers[0] | energy_source_type | [101 empty] | NATURAL_GAS | NATURAL_GAS
rmr_transformations | user | JSON_PATH:chillers[0] | id | [101 empty] | Chiller 1 | Chiller 1
rmr_transformations | user | JSON_PATH:chillers[0] | cooling_loop | [101 empty] | Chiller Loop 1 | Chiller Loop 1
rmr_transformations | user | JSON_PATH:chillers[0] | design_capacity
rmr_transformations | user | JSON_PATH:chillers[0] | energy_source_type
rmr_transformations | user | JSON_PATH:chillers[0] | full_load_efficiency
rmr_transformations | user | JSON_PATH:chillers[0] | compressor_type
rmr_transformations | user | JSON_PATH:chillers[1] | id
rmr_transformations | user | JSON_PATH:chillers[1] | cooling_loop
rmr_transformations | user | JSON_PATH:chillers[1] | design_capacity
rmr_transformations | user | JSON_PATH:chillers[2] | id
rmr_transformations | user | JSON_PATH:chillers[2] | cooling_loop
rmr_transformations | user | JSON_PATH:chillers[2] | design_capacity
rmr_transformations | user | JSON_PATH:chillers[3] | id
rmr_transformations | user | JSON_PATH:chillers[3] | cooling_loop
rmr_transformations | user | JSON_PATH:chillers[3] | design_capacity
rmr_transformations | user | JSON_PATH:heat_rejections[0] | id
rmr_transformations | user | JSON_PATH:heat_rejections[0] | loop
rmr_transformations | user | JSON_PATH:heat_rejections[0] | type
rmr_transformations | user | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature | [6 empty] | temperature | F
rmr_transformations | user | JSON_PATH:heat_rejections[0] | design_water_flowrate
rmr_transformations | user | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature | [6 empty] | temperature | F
rmr_transformations | user | JSON_PATH:heat_rejections[0] | fan_speed_control
rmr_transformations | user | JSON_PATH:heat_rejections[0] | range
rmr_transformations | user | JSON_PATH:heat_rejections[0] | reset_type
rmr_transformations | user | JSON_PATH:heat_rejections[1] | id
rmr_transformations | user | JSON_PATH:heat_rejections[1] | loop
rmr_transformations | user | JSON_PATH:heat_rejections[1] | type
rmr_transformations | user | JSON_PATH:pumps[0] | id | [101 empty] | Boiler Pump 1 | Boiler Pump 1
rmr_transformations | user | JSON_PATH:pumps[0] | loop_or_piping | [101 empty] | Boiler Loop 1 | Boiler Loop 1
rmr_transformations | user | JSON_PATH:pumps[0] | speed_control | [101 empty] | FIXED_SPEED | FIXED_SPEED
rmr_transformations | user | JSON_PATH:pumps[0] | design_electric_power
rmr_transformations | user | JSON_PATH:pumps[0] | design_flow
rmr_transformations | user | JSON_PATH:pumps[0] | design_head
rmr_transformations | user | JSON_PATH:pumps[0] | motor_efficiency
rmr_transformations | user | JSON_PATH:pumps[0] | impeller_efficiency
rmr_transformations | user | JSON_PATH:pumps[1] | id | [101 empty] | Chiller Pump 1 | Chiller Pump 1
rmr_transformations | user | JSON_PATH:pumps[1] | loop_or_piping | [101 empty] | Chiller Loop 1 | Chiller Loop 1
rmr_transformations | user | JSON_PATH:pumps[1] | speed_control | [101 empty] | FIXED_SPEED | FIXED_SPEED
rmr_transformations | user | JSON_PATH:pumps[1] | design_electric_power
rmr_transformations | user | JSON_PATH:pumps[1] | design_flow
rmr_transformations | user | JSON_PATH:pumps[2] | id | [101 empty] | Secondary CHW Pump | Secondary CHW Pump
rmr_transformations | user | JSON_PATH:pumps[2] | loop_or_piping | [101 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1
rmr_transformations | user | JSON_PATH:pumps[2] | speed_control | [101 empty] | VARIABLE_SPEED | VARIABLE_SPEED
rmr_transformations | user | JSON_PATH:fluid_loops[0] | id | [101 empty] | Boiler Loop 1 | Boiler Loop 1
rmr_transformations | user | JSON_PATH:fluid_loops[0] | type | [101 empty] | HEATING | HEATING
rmr_transformations | user | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id
rmr_transformations | user | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature | [5 empty] | temperature | F
rmr_transformations | user | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature | [5 empty] | temperature | F
rmr_transformations | user | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type
rmr_transformations | user | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction
rmr_transformations | user | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | has_integrated_waterside_economizer
rmr_transformations | user | JSON_PATH:fluid_loops[0] | child_loops[0] | id
rmr_transformations | user | JSON_PATH:fluid_loops[0] | child_loops[0] | type
rmr_transformations | user | JSON_PATH:fluid_loops[1] | id | [101 empty] | Chiller Loop 1 | Chiller Loop 1
rmr_transformations | user | JSON_PATH:fluid_loops[1] | type | [101 empty] | COOLING | COOLING
rmr_transformations | user | JSON_PATH:fluid_loops[1] | child_loops[0] | id | [100 empty] | Secondary CHW Loop 1 | Secondary CHW Loop 1
rmr_transformations | user | JSON_PATH:output | id
rmr_transformations | user | JSON_PATH:output | output_instance | id
rmr_transformations | user | JSON_PATH:output | output_instance | unmet_load_hours_heating
rmr_transformations | user | JSON_PATH:output | output_instance | unmet_load_hours_cooling
rmr_transformations | user | JSON_PATH:output | output_instance | unmet_load_hours
rmr_transformations | user | JSON_PATH:output | output_instance | unmet_occupied_load_hours_heating
rmr_transformations | user | JSON_PATH:output | output_instance | unmet_occupied_load_hours_cooling
rmr_transformations | user | JSON_PATH:output | output_instance | building_peak_cooling_load
rmr_transformations | user | JSON_PATH:fan_system | air_economizer | id
rmr_transformations | user | JSON_PATH:fan_system | air_economizer | type
rmr_transformations | user | JSON_PATH:fan_system | air_economizer | high_limit_shutoff_temperature | [5 empty] | temperature | F
rmr_transformations | user | JSON_PATH:fan_system | air_energy_recovery | id
rmr_transformations | user | JSON_PATH:fan_system | air_energy_recovery | energy_recovery_operation
rmr_transformations | user | JSON_PATH:fan_system | supply_fans[0] | id | [100 empty] | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1
rmr_transformations | user | JSON_PATH:fan_system | supply_fans[0] | specification_method
rmr_transformations | user | JSON_PATH:fan_system | supply_fans[0] | design_electric_power
rmr_transformations | user | JSON_PATH:fan_system | supply_fans[0] | design_airflow | [5 empty] | air_flow_rate | cfm
rmr_transformations | user | JSON_PATH:fan_system | return_fans[0] | id | [100 empty] | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1
rmr_transformations | user | JSON_PATH:fan_system | return_fans[0] | specification_method
rmr_transformations | user | JSON_PATH:fan_system | return_fans[0] | design_electric_power
rmr_transformations | user | JSON_PATH:fan_system | return_fans[0] | design_airflow | [5 empty] | air_flow_rate | cfm
rmr_transformations | user | JSON_PATH:fan_system | relief_fans[0] | id
rmr_transformations | user | JSON_PATH:fan_system | relief_fans[0] | specification_method
rmr_transformations | user | JSON_PATH:fan_system | relief_fans[0] | design_electric_power
rmr_transformations | user | JSON_PATH:fan_system | return_fans[1] | id
rmr_transformations | user | JSON_PATH:fan_system | return_fans[1] | specification_method
rmr_transformations | user | JSON_PATH:fan_system | return_fans[1] | design_electric_power
rmr_transformations | user | JSON_PATH:fan_system | return_fans[1] | design_airflow | [5 empty] | air_flow_rate | cfm
rmr_transformations | user | JSON_PATH:fan_system | exhaust_fans[0] | id
rmr_transformations | user | JSON_PATH:fan_system | exhaust_fans[0] | specification_method
rmr_transformations | user | JSON_PATH:fan_system | exhaust_fans[0] | design_electric_power
rmr_transformations | user | JSON_PATH:fluid_loops[0] | heating_design_and_control | id
rmr_transformations | user | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load
rmr_transformations | user | JSON_PATH:fluid_loops[1] | cooling_or_condensing_design_and_control | id
rmr_transformations | user | JSON_PATH:fluid_loops[1] | cooling_or_condensing_design_and_control | is_sized_using_coincident_load
rmr_transformations | user | JSON_PATH:schedules[0] | id
rmr_transformations | user | JSON_PATH:schedules[0] | hourly_values
rmr_transformations | user | JSON_PATH:schedules[1] | id
rmr_transformations | user | JSON_PATH:schedules[1] | hourly_values
rmr_transformations | user | JSON_PATH:schedules[2] | id
rmr_transformations | user | JSON_PATH:schedules[2] | hourly_values
rmr_transformations | user | JSON_PATH:schedules[3] | id
rmr_transformations | user | JSON_PATH:schedules[3] | hourly_values
rmr_transformations | proposed | id
rmr_transformations | proposed | weather | climate_zone | [43 empty] | CZ5A | CZ5A | CZ5A | CZ5A | CZ5A | CZ3A | CZ5A | CZ5A | CZ5A | [36 empty] | CZ5A | CZ5A | CZ5A | CZ3A | CZ5A | CZ5A | CZ5A | CZ5A | CZ5A | CZ5A | CZ5A | [25 empty] | CZ5A | CZ4A | CZ5A | CZ4A
rmr_transformations | proposed | ruleset_model_descriptions[0] | id
rmr_transformations | proposed | JSON_PATH:buildings[0] | id
rmr_transformations | proposed | JSON_PATH:buildings[0] | building_open_schedule
rmr_transformations | proposed | JSON_PATH:buildings[0] | refrigerated_casess[0] | id
rmr_transformations | proposed | JSON_PATH:buildings[0] | refrigerated_casess[0] | type
rmr_transformations | proposed | JSON_PATH: building_segments[0] | id
rmr_transformations | proposed | JSON_PATH:building_segments[0] | lighting_building_area_type
rmr_transformations | proposed | JSON_PATH:zones[0] | id
rmr_transformations | proposed | JSON_PATH:zones[0] | design_thermostat_cooling_setpoint | [6 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:zones[0] | design_thermostat_heating_setpoint | [6 empty] | temperature | F | [80 empty] | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
rmr_transformations | proposed | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule | [89 empty] | Cooling Temperature Setpoint Schedule 1
rmr_transformations | proposed | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule | [88 empty] | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1
rmr_transformations | proposed | JSON_PATH:zones[0] | air_distribution_effectiveness | [27 empty] | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 1 | 1 | 1 | 1
rmr_transformations | proposed | JSON_PATH:zones[0] | non_mechanical_cooling_fan_airflow | [6 empty] | air_flow_rate | cfm | [77 empty] | 250
rmr_transformations | proposed | JSON_PATH:zones[0] | infiltration | id
rmr_transformations | proposed | JSON_PATH:zones[0] | infiltration | multiplier_schedule
rmr_transformations | proposed | JSON_PATH:zones[0] | zonal_exhaust_fan | id
rmr_transformations | proposed | JSON_PATH:zones[0] | zonal_exhaust_fan | specification_method
rmr_transformations | proposed | JSON_PATH:zones[0] | zonal_exhaust_fan | design_electric_power
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | id | [26 empty] | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | [5 empty] | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | [36 empty] | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | [10 empty] | Space 1 | Space 1 |  |  | Space 1 | Space 1 | [5 empty] | Space 1 | Space 1 |  |  | Space 1 | Space 1 | Space 1 | Space 1
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | number_of_occupants
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | floor_area | [5 empty] | area | ft2 | [35 empty] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | [61 empty] | 1000 | 1000 | [5 empty] | 1000 | 1000
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | lighting_space_type | [26 empty] | OFFICE_ENCLOSED | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM |  | OFFICE_ENCLOSED | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | OFFICE_ENCLOSED | OFFICE_ENCLOSED | OFFICE_ENCLOSED | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | [50 empty] | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | FOOD_PREPARATION_AREA | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | [10 empty] | HEALTHCARE_FACILITY_OPERATING_ROOM |  |  |  | AUDIENCE_SEATING_AREA_GYMNASIUM | CLASSROOM_LECTURE_HALL_TRAINING_ROOM_ALL_OTHER | [5 empty] | COMPUTER_ROOM | COMPUTER_ROOM |  |  | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM |  | STORAGE_ROOM_LARGE
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | ventilation_space_type | [89 empty] | MISCELLANEOUS_SPACES_MANUFACTURING_WHERE_HAZARDOUS_MATERIALS_ARE_USED_EXCLUDES_HEAVY_INDUSTRIAL_AND_CHEMICAL_PROCESSES |  |  |  | FOOD_AND_BEVERAGE_SERVICE_KITCHEN_COOKING | [15 empty] | ANIMAL_FACILITIES_ANIMAL_IMAGING_MRI_CT_PET
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | interior_lighting[0] | id
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | interior_lighting[0] | lighting_multiplier_schedule
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | miscellaneous_equipment[0] | id
rmr_transformations | proposed | JSON_PATH:zones[0] | spaces[0] | miscellaneous_equipment[0] | multiplier_schedule
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | id
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | has_demand_control_ventilation | [26 empty] | false | false | false | true | true | false | false | false | false | false | false
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | type
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | primary_airflow | [5 empty] | air_flow_rate | cfm | [52 empty] | 2000 | 2000 | 2000 | 2000 | 1000 | 1000 | 1000 | 500 | 500 | 500 | 500 | [15 empty] | 1000 | 1000 |  |  |  | 5000
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | minimum_outdoor_airflow | [5 empty] | air_flow_rate | cfm | [19 empty] | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 400 | 250 | 250 | 250 | [27 empty] | 200 | 200 | 100 | 25 | 100 | 100 | [20 empty] | 3750
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | minimum_outdoor_airflow_multiplier_schedule | [26 empty] | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | heating_source
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | heating_from_loop
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | cooling_source
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | fan | id
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | fan_configuration
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | supply_design_cooling_setpoint_temperature | [5 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:zones[0] | terminals[0] | supply_design_heating_setpoint_temperature | [5 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:zones[1] | id
rmr_transformations | proposed | JSON_PATH:zones[1] | design_thermostat_cooling_setpoint | [6 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:zones[1] | design_thermostat_heating_setpoint | [6 empty] | temperature | F | [80 empty] | 70 |  | 70 |  | 70 | 70 |  | 70 | 70 | 70 | 70
rmr_transformations | proposed | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule
rmr_transformations | proposed | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule | [88 empty] | Heating Temperature Setpoint Schedule 1 |  | Heating Temperature Setpoint Schedule 1 |  | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 |  | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1
rmr_transformations | proposed | JSON_PATH:zones[1] | air_distribution_effectiveness | [27 empty] | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 1 | 1 | 1 | 1
rmr_transformations | proposed | JSON_PATH:zones[1] | spaces[0] | id | [26 empty] | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | [6 empty] | Space 2 |  |  |  | Space 2 |  | Space 2 | Space 2 | [36 empty] | Space 3 |  | Space 3 |  | Space 3 | Space 3 |  | Space 3 | Space 3 | Space 3 | Space 3
rmr_transformations | proposed | JSON_PATH:zones[1] | spaces[0] | lighting_space_type | [26 empty] | OFFICE_ENCLOSED |  |  | OFFICE_ENCLOSED |  | OFFICE_ENCLOSED |  | OFFICE_ENCLOSED | OFFICE_ENCLOSED | OFFICE_ENCLOSED | [51 empty] | OFFICE_OPEN_PLAN |  | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM |  | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN |  | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN
rmr_transformations | proposed | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule
rmr_transformations | proposed | JSON_PATH:zones[1] | spaces[0] | floor_area | [43 empty] | 500 |  |  |  | 500 |  | 500 | 500
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | id
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | has_demand_control_ventilation | [26 empty] | false | false | false | false | false | false | false | false | false | false | false
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | type
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | primary_airflow | [5 empty] | air_flow_rate | cfm | [52 empty] | 2000 |  | 2000 |  | 1000 |  |  | 500 | 500 | 500 | 500
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | minimum_outdoor_airflow | [5 empty] | air_flow_rate | cfm | [19 empty] | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 400 | 250 | 250 | 250 | [29 empty] | 100 | 25 | 100 | 100
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | minimum_outdoor_airflow_multiplier_schedule | [26 empty] | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | heating_source
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | heating_from_loop
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | cooling_source
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | cooling_from_loop
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | fan | id
rmr_transformations | proposed | JSON_PATH:zones[1] | terminals[0] | fan_configuration
rmr_transformations | proposed | JSON_PATH:zones[1] | infiltration | id
rmr_transformations | proposed | JSON_PATH:zones[1] | infiltration | multiplier_schedule
rmr_transformations | proposed | JSON_PATH:spaces[1] | id | [88 empty] | Space 2 | Space 2 | Space 2 |  | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | [25 empty] | Space 2 |  |  | Space 2
rmr_transformations | proposed | JSON_PATH:spaces[1] | lighting_space_type | [88 empty] | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM |  | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN |  | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | [25 empty] | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM |  |  | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM
rmr_transformations | proposed | JSON_PATH:spaces[1] | ventilation_space_type | [94 empty] | FOOD_AND_BEVERAGE_SERVICE_KITCHEN_COOKING
rmr_transformations | proposed | JSON_PATH:spaces[1] | occupant_multiplier_schedule
rmr_transformations | proposed | JSON_PATH:spaces[1] | interior_lighting[0] | id
rmr_transformations | proposed | JSON_PATH:spaces[1] | interior_lighting[0] | lighting_multiplier_schedule
rmr_transformations | proposed | JSON_PATH:spaces[1] | miscellaneous_equipment[0] | id
rmr_transformations | proposed | JSON_PATH:spaces[1] | miscellaneous_equipment[0] | multiplier_schedule
rmr_transformations | proposed | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id
rmr_transformations | proposed | JSON_PATH:cooling_system | id | [76 empty] | NonMech_System | NonMech_System
rmr_transformations | proposed | JSON_PATH:cooling_system | type | [76 empty] | NON_MECHANICAL | NON_MECHANICAL
rmr_transformations | proposed | JSON_PATH:cooling_system | is_autosized | [76 empty] | true | true
rmr_transformations | proposed | JSON_PATH:cooling_system | oversizing_factor
rmr_transformations | proposed | JSON_PATH:cooling_system | chilled_water_loop
rmr_transformations | proposed | JSON_PATH:cooling_system | dehumidification_type | [93 empty] | SERIES_HEAT_RECOVERY
rmr_transformations | proposed | JSON_PATH:heating_system | id
rmr_transformations | proposed | JSON_PATH:heating_system | type
rmr_transformations | proposed | JSON_PATH:heating_system | is_autosized
rmr_transformations | proposed | JSON_PATH:heating_system | oversizing_factor
rmr_transformations | proposed | JSON_PATH:heating_system | energy_source_type
rmr_transformations | proposed | JSON_PATH:heating_system | hot_water_loop
rmr_transformations | proposed | JSON_PATH:preheat_system | id
rmr_transformations | proposed | JSON_PATH:preheat_system | type
rmr_transformations | proposed | JSON_PATH:preheat_system | hot_water_loop
rmr_transformations | proposed | JSON_PATH:fan_system | id
rmr_transformations | proposed | JSON_PATH:fan_system | fan_control
rmr_transformations | proposed | JSON_PATH:fan_system | operation_during_occupied | [101 empty] | CONTINUOUS | CYCLING | CYCLING | KEEP_OFF | CONTINUOUS | CYCLING | CYCLING | KEEP_OFF
rmr_transformations | proposed | JSON_PATH:fan_system | operation_during_unoccupied | [109 empty] | CONTINUOUS | KEEP_OFF |  |  | CYCLING | KEEP_OFF | [5 empty] | CONTINUOUS | CYCLING
rmr_transformations | proposed | JSON_PATH:fan_system | minimum_outdoor_airflow | [6 empty] | air_flow_rate | cfm | [52 empty] | 1000 | 5000 | 1000 | 1000 | 1000 | 200 | 200 | 200 | 50 | 200 | 200 | 25 | 25 | 325 | 325 | 25 | [12 empty] | 3750 | 3750 | 3750 | 3750 | 3750 | 3750 | 3750 | 3750 | 3450 | 3750 | 3750 |  |  | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | 100 | 100 |  |  | 100 | 100 | [5 empty] | 100 | 100 |  |  | 4000 | 4000 | 4000 | 4000
rmr_transformations | proposed | JSON_PATH:fan_system | maximum_outdoor_airflow | [6 empty] | air_flow_rate | cfm | [80 empty] | 3750 | 3750 | 3750 | 3750 | 3750 | 3750 | 3750 | 3750 | 3450 | 3750 | 3750
rmr_transformations | proposed | JSON_PATH:fan_system | demand_control_ventilation_control | [27 empty] | NONE | NONE | NONE | CO2_ZONE | CO2_ZONE | NONE | NONE | NONE | NONE | NONE | NONE
rmr_transformations | proposed | JSON_PATH:boilers[0] | id
rmr_transformations | proposed | JSON_PATH:boilers[0] | loop
rmr_transformations | proposed | JSON_PATH:boilers[0] | energy_source_type
rmr_transformations | proposed | JSON_PATH:chillers[0] | id
rmr_transformations | proposed | JSON_PATH:chillers[0] | cooling_loop
rmr_transformations | proposed | JSON_PATH:chillers[0] | design_capacity
rmr_transformations | proposed | JSON_PATH:chillers[0] | energy_source_type
rmr_transformations | proposed | JSON_PATH:chillers[0] | full_load_efficiency
rmr_transformations | proposed | JSON_PATH:chillers[0] | compressor_type
rmr_transformations | proposed | JSON_PATH:chillers[1] | id
rmr_transformations | proposed | JSON_PATH:chillers[1] | cooling_loop
rmr_transformations | proposed | JSON_PATH:chillers[1] | design_capacity
rmr_transformations | proposed | JSON_PATH:chillers[2] | id
rmr_transformations | proposed | JSON_PATH:chillers[2] | cooling_loop
rmr_transformations | proposed | JSON_PATH:chillers[2] | design_capacity
rmr_transformations | proposed | JSON_PATH:chillers[3] | id
rmr_transformations | proposed | JSON_PATH:chillers[3] | cooling_loop
rmr_transformations | proposed | JSON_PATH:chillers[3] | design_capacity
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | id
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | loop
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | type
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature | [6 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | design_water_flowrate
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature | [6 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | fan_speed_control
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | range
rmr_transformations | proposed | JSON_PATH:heat_rejections[0] | reset_type
rmr_transformations | proposed | JSON_PATH:heat_rejections[1] | id
rmr_transformations | proposed | JSON_PATH:heat_rejections[1] | loop
rmr_transformations | proposed | JSON_PATH:heat_rejections[1] | type
rmr_transformations | proposed | JSON_PATH:pumps[0] | id
rmr_transformations | proposed | JSON_PATH:pumps[0] | loop_or_piping
rmr_transformations | proposed | JSON_PATH:pumps[0] | speed_control
rmr_transformations | proposed | JSON_PATH:pumps[0] | design_electric_power
rmr_transformations | proposed | JSON_PATH:pumps[0] | design_flow
rmr_transformations | proposed | JSON_PATH:pumps[0] | design_head
rmr_transformations | proposed | JSON_PATH:pumps[0] | motor_efficiency
rmr_transformations | proposed | JSON_PATH:pumps[0] | impeller_efficiency
rmr_transformations | proposed | JSON_PATH:pumps[1] | id
rmr_transformations | proposed | JSON_PATH:pumps[1] | loop_or_piping
rmr_transformations | proposed | JSON_PATH:pumps[1] | speed_control
rmr_transformations | proposed | JSON_PATH:pumps[1] | design_electric_power
rmr_transformations | proposed | JSON_PATH:pumps[1] | design_flow
rmr_transformations | proposed | JSON_PATH:pumps[2] | id
rmr_transformations | proposed | JSON_PATH:pumps[2] | loop_or_piping
rmr_transformations | proposed | JSON_PATH:pumps[2] | speed_control
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | id
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | type
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature | [5 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature | [5 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | child_loops[0] | id
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | child_loops[0] | type
rmr_transformations | proposed | JSON_PATH:fluid_loops[1] | id
rmr_transformations | proposed | JSON_PATH:fluid_loops[1] | type
rmr_transformations | proposed | JSON_PATH:fluid_loops[1] | child_loops[0] | id
rmr_transformations | proposed | JSON_PATH:output | id |  |  | Output | Output 1 | ASHRAE229 1 | id | [13 empty] | Output 1 | Output 1 | Output 1 | Output 1
rmr_transformations | proposed | JSON_PATH:output | output_instance | id |  | Output | Output 1 | OutputInstance | id | [13 empty] | Output Instance 1 | Output Instance 1 | Output Instance 1 | Output Instance 1
rmr_transformations | proposed | JSON_PATH:output | output_instance | unmet_load_hours_heating |  | Output | Output 1 | OutputInstance | unmet_load_hours_heating | [13 empty] | 0 | 50 | 400 | 200
rmr_transformations | proposed | JSON_PATH:output | output_instance | unmet_load_hours_cooling |  | Output | Output 1 | OutputInstance | unmet_load_hours_cooling | [13 empty] | 0 | 100 | 400 | 500
rmr_transformations | proposed | JSON_PATH:output | output_instance | unmet_load_hours |  | Output | Output 1 | OutputInstance | unmet_load_hours | [13 empty] | 200 | 350 | 350 | 350
rmr_transformations | proposed | JSON_PATH:output | output_instance | unmet_occupied_load_hours_heating |  | Output | Output 1 | OutputInstance | unmet_occupied_load_hours_heating | [13 empty] | 0 | 0 | 0 | 0
rmr_transformations | proposed | JSON_PATH:output | output_instance | unmet_occupied_load_hours_cooling |  | Output | Output 1 | OutputInstance | unmet_occupied_load_hours_cooling | [13 empty] | 0 | 0 | 0 | 0
rmr_transformations | proposed | JSON_PATH:output | output_instance | building_peak_cooling_load |  | Output | Output 1 | OutputInstance | building_peak_cooling_load | cooling_capacity | ton | [11 empty] | 200 | 200 | 200 | 200
rmr_transformations | proposed | JSON_PATH:fan_system | air_economizer | id | [42 empty] | Air Economizer 1 | Air Economizer 1
rmr_transformations | proposed | JSON_PATH:fan_system | air_economizer | type | [42 empty] | ENTHALPY | ENTHALPY
rmr_transformations | proposed | JSON_PATH:fan_system | air_economizer | high_limit_shutoff_temperature | [5 empty] | temperature | F
rmr_transformations | proposed | JSON_PATH:fan_system | air_energy_recovery | id | [87 empty] | Air Energy Recovery 1 |  |  |  |  | Air Energy Recovery 1
rmr_transformations | proposed | JSON_PATH:fan_system | air_energy_recovery | energy_recovery_operation | [87 empty] | WHEN_MINIMUM_OUTSIDE_AIR |  |  |  |  | NONE
rmr_transformations | proposed | JSON_PATH:fan_system | supply_fans[0] | id | [85 empty] | Supply fan 1 | Supply fan 1
rmr_transformations | proposed | JSON_PATH:fan_system | supply_fans[0] | specification_method | [64 empty] | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE |  | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | [10 empty] | SIMPLE | SIMPLE
rmr_transformations | proposed | JSON_PATH:fan_system | supply_fans[0] | design_electric_power | [64 empty] | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | [10 empty] | 100 | 100
rmr_transformations | proposed | JSON_PATH:fan_system | supply_fans[0] | design_airflow | [5 empty] | air_flow_rate | cfm | [57 empty] | 1000 | 1000 | 1000 | 1000 | 1000 | [16 empty] | 1000 | 1000 | 5000 | 5000 | 5000 |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
rmr_transformations | proposed | JSON_PATH:fan_system | return_fans[0] | id | [85 empty] | Return fan 1 | Return fan 1
rmr_transformations | proposed | JSON_PATH:fan_system | return_fans[0] | specification_method | [64 empty] | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE |  | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | [10 empty] | SIMPLE | SIMPLE
rmr_transformations | proposed | JSON_PATH:fan_system | return_fans[0] | design_electric_power | [64 empty] | 0 | 0 | 90 | 95 | 80 |  | 100 | 100 | 100 | 100 | 100 | [10 empty] | 50 | 50
rmr_transformations | proposed | JSON_PATH:fan_system | return_fans[0] | design_airflow | [5 empty] | air_flow_rate | cfm | [57 empty] | 0 | 0 | 900 | 950 | 800 | [16 empty] | 800 | 800
rmr_transformations | proposed | JSON_PATH:fan_system | relief_fans[0] | id | [85 empty] | Relief fan 1 | Relief fan 1
rmr_transformations | proposed | JSON_PATH:fan_system | relief_fans[0] | specification_method | [85 empty] | SIMPLE | SIMPLE
rmr_transformations | proposed | JSON_PATH:fan_system | relief_fans[0] | design_electric_power | [85 empty] | 0 | 0
rmr_transformations | proposed | JSON_PATH:fan_system | exhaust_fans[0] | id | [85 empty] | Exhaust fan 1 | Exhaust fan 1 |  |  |  |  | Exhaust Fan 1 |  |  | Exhaust Fan 1
rmr_transformations | proposed | JSON_PATH:fan_system | exhaust_fans[0] | specification_method | [85 empty] | SIMPLE | SIMPLE |  |  |  |  | SIMPLE |  |  | SIMPLE
rmr_transformations | proposed | JSON_PATH:fan_system | exhaust_fans[0] | design_electric_power | [85 empty] | 50 | 50
rmr_transformations | proposed | JSON_PATH:fan_system | exhaust_fans[0] | design_airflow | [5 empty] | air_flow_rate | cfm | [84 empty] | 3000 |  |  | 2500
rmr_transformations | proposed | JSON_PATH:fan_system | exhaust_fans[1] | id | [94 empty] | Exhaust Fan 2
rmr_transformations | proposed | JSON_PATH:fan_system | exhaust_fans[1] | specification_method | [94 empty] | SIMPLE
rmr_transformations | proposed | JSON_PATH:fan_system | exhaust_fans[1] | design_electric_power
rmr_transformations | proposed | JSON_PATH:fan_system | exhaust_fans[1] | design_airflow | [5 empty] | air_flow_rate | cfm | [87 empty] | 2500
rmr_transformations | proposed | JSON_PATH:fan_system | return_fans[1] | id
rmr_transformations | proposed | JSON_PATH:fan_system | return_fans[1] | specification_method
rmr_transformations | proposed | JSON_PATH:fan_system | return_fans[1] | design_electric_power
rmr_transformations | proposed | JSON_PATH:fan_system | return_fans[1] | design_airflow | [5 empty] | air_flow_rate | cfm
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | heating_design_and_control | id
rmr_transformations | proposed | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load
rmr_transformations | proposed | JSON_PATH:fluid_loops[1] | cooling_or_condensing_design_and_control | id
rmr_transformations | proposed | JSON_PATH:fluid_loops[1] | cooling_or_condensing_design_and_control | is_sized_using_coincident_load
rmr_transformations | proposed | JSON_PATH:schedules[0] | id | [27 empty] | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | [50 empty] | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | [25 empty] | Min OA CFM Schedule | Min OA CFM Schedule | Min OA CFM Schedule | Min OA CFM Schedule
rmr_transformations | proposed | JSON_PATH:schedules[0] | hourly_values | [27 empty] | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-0.929 | SCHEDULE:CONSTANT-1.0 | [50 empty] | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-13 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-13 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | [25 empty] | SCHEDULE:CONSTANT-1888 | SCHEDULE:CONSTANT-1888 | SCHEDULE:CONSTANT-1888 | SCHEDULE:CONSTANT-1888
rmr_transformations | proposed | JSON_PATH:schedules[0] | type | [88 empty] | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE
rmr_transformations | proposed | JSON_PATH:schedules[1] | id | [124 empty] | FLOW_RATE | FLOW_RATE | FLOW_RATE | FLOW_RATE
rmr_transformations | proposed | JSON_PATH:schedules[1] | hourly_values
rmr_transformations | proposed | JSON_PATH:schedules[2] | id
rmr_transformations | proposed | JSON_PATH:schedules[2] | hourly_values
rmr_transformations | proposed | JSON_PATH:schedules[3] | id
rmr_transformations | proposed | JSON_PATH:schedules[3] | hourly_values
rmr_transformations | proposed | JSON_PATH:schedules[4] | id
rmr_transformations | proposed | JSON_PATH:schedules[4] | hourly_values
rmr_transformations | baseline | id
rmr_transformations | baseline | weather | climate_zone | [43 empty] | CZ5A | CZ5A | CZ5A | CZ5A | CZ5A | CZ3A | CZ5A | CZ5A | CZ5A |  |  |  | CZ3C | CZ3C | CZ3C | CZ3C | CZ0A | [28 empty] | CZ5A | CZ5A | CZ5A | CZ3A | CZ5A | CZ5A | CZ5A | CZ5A | CZ5A | CZ5A | CZ5A | [25 empty] | CZ5A | CZ4A | CZ5A | CZ4A
rmr_transformations | baseline | ruleset_model_descriptions[0] | id
rmr_transformations | baseline | JSON_PATH:buildings[0] | id
rmr_transformations | baseline | JSON_PATH:buildings[0] | building_open_schedule
rmr_transformations | baseline | JSON_PATH:buildings[0] | refrigerated_casess[0] | id | [49 empty] | Refrigerated Case 1 | Refrigerated Case 1
rmr_transformations | baseline | JSON_PATH:buildings[0] | refrigerated_casess[0] | type | [49 empty] | COMMERCIAL_REFRIGERATION | COMMERCIAL_REFRIGERATION
rmr_transformations | baseline | JSON_PATH: building_segments[0] | id
rmr_transformations | baseline | JSON_PATH:building_segments[0] | lighting_building_area_type |  |  | Building Segment | Building Segment 1 | Building 1 | lighting_building_area_type | [9 empty] | DORMITORY | DORMITORY | DORMITORY | DORMITORY | [31 empty] | RETAIL | RETAIL
rmr_transformations | baseline | JSON_PATH:zones[0] | id
rmr_transformations | baseline | JSON_PATH:zones[0] | design_thermostat_cooling_setpoint |  |  | Zone | Zone 1 | Building Segment 1 | design_thermostat_cooling_setpoint | temperature | F | [52 empty] | 80 | 78 | 75 | 72 | 72
rmr_transformations | baseline | JSON_PATH:zones[0] | design_thermostat_heating_setpoint |  |  | Zone | Zone 1 | Building Segment 1 | design_thermostat_heating_setpoint | temperature | F | [52 empty] | 70 | 62 | 70 | 68 | 68 | [6 empty] | 65 | 65 | 65 | 65 | 65 | [12 empty] | 70 | 55 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
rmr_transformations | baseline | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule | [89 empty] | Cooling Temperature Setpoint Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule | [88 empty] | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[0] | air_distribution_effectiveness | [27 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
rmr_transformations | baseline | JSON_PATH:zones[0] | infiltration | id |  | Zone | Zone 1 | Building Segment 1 | id | [9 empty] | Infiltration 1 | Infiltration 1 | Infiltration 1 | Infiltration 1
rmr_transformations | baseline | JSON_PATH:zones[0] | infiltration | multiplier_schedule |  | Zone | Zone 1 | Building Segment 1 | multiplier_schedule | [9 empty] | Infiltration Schedule 1 | Infiltration Schedule 1 | Infiltration Schedule 1 | Infiltration Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[0] | zonal_exhaust_fan | id |  | Space | Space 1 | Zone 1 | id | [73 empty] | Zone exhaust fan 1 | Zone exhaust fan 1 | Zone exhaust fan 1 | Zone exhaust fan 1 | Zone exhaust fan 1 | Zone exhaust fan 1 | Zone exhaust fan 1 |  |  |  | Zonal airflow 1 | Zonal airflow 1 | Zonal airflow 1 | Zonal airflow 1 | Zonal airflow 1 | Zonal airflow 1 | Zonal airflow 1 |  | Zonal airflow 1 | Zonal airflow 1
rmr_transformations | baseline | JSON_PATH:zones[0] | zonal_exhaust_fan | specification_method |  | Space | Space 1 | Zone 1 | specification_method | [73 empty] | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE
rmr_transformations | baseline | JSON_PATH:zones[0] | zonal_exhaust_fan | design_electric_power |  | Space | Space 1 | Zone 1 | design_electric_power | electric_power | W | [71 empty] | 59 | 56 | 80 | 59 | 80 | 60 | 60
rmr_transformations | baseline | JSON_PATH:zones[0] | zonal_exhaust_fan | design_airflow | [5 empty] | air_flow_rate | cfm | [81 empty] | 4000 | 4000 | 4000 | 500 | 4000 | 4000 | 500 |  | 4000 | 4000
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | id |  | Zone | Space 1 | Building Segment 1 | [10 empty] | Space 1 | Space 1 | Space 1 | Space 1 | [8 empty] | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 |  |  |  | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | [5 empty] | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | [6 empty] | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | [12 empty] | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | [12 empty] | Space 1 | Space 1 |  |  | Space 1 | Space 1 | [5 empty] | Space 1 | Space 1 | Space 1 | Space 1 | Space 1 | Space 1
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | number_of_occupants | [37 empty] | 150 | 20
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule | [14 empty] | Occupancy Schedule 1 | Occupancy Schedule 1 | Occupancy Schedule 1 | Occupancy Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2 | [30 empty] | 1000 | 1000 |  |  |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | [5 empty] | 1000 | 1000 | 1000 | 1000 | 1000 | [50 empty] | 1000 | 1000 | [5 empty] | 1000 | 1000
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | lighting_space_type |  | Zone | Space 1 | Building Segment 1 | [10 empty] | DWELLING_UNIT | DWELLING_UNIT | GUEST_ROOM | [9 empty] | OFFICE_ENCLOSED | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM |  | OFFICE_ENCLOSED | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | OFFICE_ENCLOSED | OFFICE_ENCLOSED | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | [5 empty] | OFFICE_ENCLOSED | OFFICE_ENCLOSED | COMPUTER_ROOM | COMPUTER_ROOM | OFFICE_ENCLOSED | OFFICE_ENCLOSED | OFFICE_ENCLOSED |  |  | COMPUTER_ROOM | COMPUTER_ROOM | COMPUTER_ROOM | [5 empty] | OFFICE_ENCLOSED | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | OFFICE_ENCLOSED | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | OFFICE_ENCLOSED | [6 empty] | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | [12 empty] | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | FOOD_PREPARATION_AREA | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | [12 empty] | HEALTHCARE_FACILITY_OPERATING_ROOM |  |  |  | AUDIENCE_SEATING_AREA_GYMNASIUM | CLASSROOM_LECTURE_HALL_TRAINING_ROOM_ALL_OTHER | [5 empty] | COMPUTER_ROOM | COMPUTER_ROOM | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM |  | STORAGE_ROOM_LARGE
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | ventilation_space_type |  | Zone | Space 1 | Building Segment 1 | [10 empty] | TRANSIENT_RESIDENTIAL_DWELLING_UNIT | TRANSIENT_RESIDENTIAL_DWELLING_UNIT | TRANSIENT_RESIDENTIAL_DWELLING_UNIT | [94 empty] | ANIMAL_FACILITIES_ANIMAL_IMAGING_MRI_CT_PET
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | interior_lighting[0] | id | Space | Space 1 | Zone 1 | id | [9 empty] | Interior Lighting 1 | Interior Lighting 1 | Interior Lighting 1 | Interior Lighting 1
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | interior_lighting[0] | lighting_multiplier_schedule | Space | Space 1 | Zone 1 | lighting_multiplier_schedule | [9 empty] | Lighting Schedule 1 | Lighting Schedule 1 | Lighting Schedule 1 | Lighting Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | miscellaneous_equipment[0] | id | Space | Space 1 | Zone 1 | id | [9 empty] | Miscellaneous Schedule 1 | Miscellaneous Schedule 1 | Miscellaneous Schedule 1 | Miscellaneous Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | miscellaneous_equipment[0] | multiplier_schedule | Space | Space 1 | Zone 1 | multiplier_schedule | [9 empty] | Misc Schedule 1 | Misc Schedule 1 | Misc Schedule 1 | Misc Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | id
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | has_demand_control_ventilation | [26 empty] | false | false | false | false | false | false | false | false | false | false | false
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | type
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | primary_airflow | [5 empty] | air_flow_rate | cfm | [52 empty] | 2500 | 5000 | 2500 | 5000 | 500 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 250 | 250 | 300 | 250 | 250 | [10 empty] | 1000 | 1000 |  |  |  | 5000
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | minimum_outdoor_airflow | [5 empty] | air_flow_rate | cfm | [19 empty] | 250 | 250 | 250 | 400 | 400 | 400 | 400 | 250 | 400 | 250 | 400 | [27 empty] | 200 | 200 | 200 | 50 | 200 | 200 | [20 empty] | 3750
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | minimum_outdoor_airflow_multiplier_schedule | [26 empty] | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | heating_source
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | heating_from_loop
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | cooling_source
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | fan | id
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | fan | specification_method | [69 empty] | SIMPLE | SIMPLE
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | fan | design_electric_power | [69 empty] | 25 | 25
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | fan | design_airflow
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | fan | is_airflow_autosized
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | fan_configuration
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | supply_design_cooling_setpoint_temperature |  | Zone | Terminal 1 | Building Segment 1 | supply_design_cooling_setpoint_temperature | temperature | F | [52 empty] | 60 | 55 | 55 | 52 | 53
rmr_transformations | baseline | JSON_PATH:zones[0] | terminals[0] | supply_design_heating_setpoint_temperature |  | Zone | Terminal 1 | Building Segment 1 | supply_design_heating_setpoint_temperature | temperature | F | [52 empty] | 90 | 85 | 90 | 88 | 87 | [6 empty] | 105 | 85 | 95 | 105 | 105
rmr_transformations | baseline | JSON_PATH:zones[1] | id
rmr_transformations | baseline | JSON_PATH:zones[1] | design_thermostat_cooling_setpoint | [6 empty] | temperature | F | [52 empty] | 80 |  | 75 |  | 72
rmr_transformations | baseline | JSON_PATH:zones[1] | design_thermostat_heating_setpoint | [6 empty] | temperature | F | [52 empty] | 70 |  | 70 |  | 68 | [23 empty] | 70 |  | 70 |  | 70 | 70 |  | 70 | 70 | 70 | 70
rmr_transformations | baseline | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule | [88 empty] | Heating Temperature Setpoint Schedule 1 |  | Heating Temperature Setpoint Schedule 1 |  | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 |  | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[1] | air_distribution_effectiveness | [27 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | id | [26 empty] | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | Space 2 | [22 empty] | Space 2 |  | Space 2 |  | Space 2 | [32 empty] | Space 3 | Space 3
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | lighting_space_type | [26 empty] | OFFICE_ENCLOSED |  |  | OFFICE_ENCLOSED |  | OFFICE_ENCLOSED |  | OFFICE_ENCLOSED | OFFICE_ENCLOSED | [24 empty] | OFFICE_ENCLOSED |  | OFFICE_ENCLOSED |  | OFFICE_ENCLOSED | [32 empty] | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | floor_area
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | id
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | has_demand_control_ventilation | [26 empty] | false | false | false | false | false | false | false | false | false | false | false
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | type
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | primary_airflow | [59 empty] | 2500 |  | 2500 |  | 500
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | minimum_outdoor_airflow | [5 empty] | air_flow_rate | cfm | [19 empty] | 250 | 250 | 250 | 400 | 400 | 400 | 400 | 250 | 400 | 250 | 400
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | minimum_outdoor_airflow_multiplier_schedule | [26 empty] | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | heating_source
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | heating_from_loop
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | cooling_source
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | cooling_from_loop
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | fan | id
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | fan_configuration
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | supply_design_cooling_setpoint_temperature | [5 empty] | temperature | F | [52 empty] | 60 |  | 55 |  | 53
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | supply_design_heating_setpoint_temperature | [5 empty] | temperature | F | [52 empty] | 90 |  | 90 |  | 87
rmr_transformations | baseline | JSON_PATH:zones[1] | infiltration | id |  | Zone | Zone 2 | Building Segment 1 | id | [9 empty] | Infiltration 2 | Infiltration 2 | Infiltration 2 | Infiltration 2
rmr_transformations | baseline | JSON_PATH:zones[1] | infiltration | multiplier_schedule |  | Zone | Zone 2 | Building Segment 1 | multiplier_schedule | [9 empty] | Infiltration Schedule 1 | Infiltration Schedule 1 | Infiltration Schedule 1 | Infiltration Schedule 1
rmr_transformations | baseline | JSON_PATH:spaces[1] | id |  |  | Space | Space 2 | Zone 2 | id | [9 empty] | Space 2 | Space 2 | Space 2 | Space 2 | [69 empty] | Space 2 | Space 2 | Space 2 |  | Space 2 | Space 2 |  | Space 2 | Space 2 | Space 2 | Space 2 | [25 empty] | Space 2 | Space 2 | Space 2 | Space 2
rmr_transformations | baseline | JSON_PATH:spaces[1] | lighting_space_type |  |  | Space | Space 2 | Zone 2 | lighting_space_type | [9 empty] | DWELLING_UNIT | DWELLING_UNIT | DWELLING_UNIT | DWELLING_UNIT | [69 empty] | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN |  | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN |  | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | OFFICE_OPEN_PLAN | [25 empty] | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM |  |  | LABORATORY_EXCEPT_IN_OR_AS_A_CLASSROOM
rmr_transformations | baseline | JSON_PATH:spaces[1] | ventilation_space_type |  |  | Space | Space 2 | Zone 2 | ventilation_space_type | [9 empty] | TRANSIENT_RESIDENTIAL_DWELLING_UNIT | TRANSIENT_RESIDENTIAL_DWELLING_UNIT | TRANSIENT_RESIDENTIAL_DWELLING_UNIT | TRANSIENT_RESIDENTIAL_DWELLING_UNIT
rmr_transformations | baseline | JSON_PATH:spaces[1] | occupant_multiplier_schedule |  |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule | [9 empty] | Occupancy Schedule 1 | Occupancy Schedule 1 | Occupancy Schedule 1 | Occupancy Schedule 1
rmr_transformations | baseline | JSON_PATH:spaces[1] | interior_lighting[0] | id |  | Space | Space 2 | Zone 2 | id | [9 empty] | Interior Lighting 2 | Interior Lighting 2 | Interior Lighting 2 | Interior Lighting 2
rmr_transformations | baseline | JSON_PATH:spaces[1] | interior_lighting[0] | lighting_multiplier_schedule |  | Space | Space 2 | Zone 2 | lighting_multiplier_schedule | [9 empty] | Lighting Schedule 1 | Lighting Schedule 1 | Lighting Schedule 1 | Lighting Schedule 1
rmr_transformations | baseline | JSON_PATH:spaces[1] | miscellaneous_equipment[0] | id |  | Space | Space 2 | Zone 2 | id | [9 empty] | Miscellaneous Schedule 2 | Miscellaneous Schedule 2 | Miscellaneous Schedule 2 | Miscellaneous Schedule 2
rmr_transformations | baseline | JSON_PATH:spaces[1] | miscellaneous_equipment[0] | multiplier_schedule |  | Space | Space 2 | Zone 2 | multiplier_schedule | [9 empty] | Misc Schedule 1 | Misc Schedule 1 | Misc Schedule 1 | Misc Schedule 1
rmr_transformations | baseline | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id
rmr_transformations | baseline | JSON_PATH:cooling_system | id | [76 empty] | NonMech_System | NonMech_System
rmr_transformations | baseline | JSON_PATH:cooling_system | type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  |  |  | DIRECT_EXPANSION | [65 empty] | NON_MECHANICAL | NON_MECHANICAL
rmr_transformations | baseline | JSON_PATH:cooling_system | is_autosized |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | is_autosized |  |  | true |  | true | true | [64 empty] | true | true
rmr_transformations | baseline | JSON_PATH:cooling_system | oversizing_factor |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | oversizing_factor |  |  | 0.15 |  | 0.15 | 0
rmr_transformations | baseline | JSON_PATH:cooling_system | chilled_water_loop
rmr_transformations | baseline | JSON_PATH:heating_system | id
rmr_transformations | baseline | JSON_PATH:heating_system | type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  |  | FURNACE |  |  | OTHER
rmr_transformations | baseline | JSON_PATH:heating_system | is_autosized |  |  | HeatingSystem | Heating System 1 | HVAC 1 | is_autosized |  |  | true | true |  | true
rmr_transformations | baseline | JSON_PATH:heating_system | oversizing_factor |  |  | HeatingSystem | Heating System 1 | HVAC 1 | oversizing_factor |  |  | 0.25 | 0.25 |  | 0
rmr_transformations | baseline | JSON_PATH:heating_system | energy_source_type
rmr_transformations | baseline | JSON_PATH:heating_system | hot_water_loop
rmr_transformations | baseline | JSON_PATH:preheat_system | id
rmr_transformations | baseline | JSON_PATH:preheat_system | type
rmr_transformations | baseline | JSON_PATH:preheat_system | hot_water_loop
rmr_transformations | baseline | JSON_PATH:fan_system | id
rmr_transformations | baseline | JSON_PATH:fan_system | fan_control
rmr_transformations | baseline | JSON_PATH:fan_system | operation_during_occupied |  |  | FanSystem | Fan System 1 | HVAC 1 | operation_during_occupied | [99 empty] | CONTINUOUS | CYCLING | CYCLING | KEEP_OFF
rmr_transformations | baseline | JSON_PATH:fan_system | operation_during_unoccupied |  |  | FanSystem | Fan System 1 | HVAC 1 | operation_during_unoccupied | [105 empty] | CONTINUOUS | KEEP_OFF |  |  | CYCLING | KEEP_OFF | [5 empty] | CONTINUOUS | CYCLING
rmr_transformations | baseline | JSON_PATH:fan_system | minimum_outdoor_airflow |  |  | FanSystem | Fan System 1 | HVAC 1 | minimum_outdoor_airflow | air_flow_rate | cfm | [30 empty] | 3500 | 2800 | [20 empty] | 1000 | 5000 | 10000 | 1000 | 450 | 200 | 200 | 200 | 50 | 200 | 200 | 0 | 0 | 300 | 300 | 0 | [12 empty] | 4500 | 4500 | 4500 | 4500 | 3750 | 3750 | 3750 | 3750 | 3450 | 3750 | 10000 | [6 empty] | 100 | 100 | 0 | 0 |  |  | 100 | 100 |  |  | 100 | 100 | [5 empty] | 100 | 100 |  |  |  |  | 7000
rmr_transformations | baseline | JSON_PATH:fan_system | maximum_outdoor_airflow |  |  | FanSystem | Fan System 1 | HVAC 1 | maximum_outdoor_airflow | air_flow_rate | cfm | [80 empty] | 5000 | 5000 | 5000 | 5000 | 3750 | 3750 | 3750 | 20000 | 3450 | 3750 | 3750 | [29 empty] | 10000
rmr_transformations | baseline | JSON_PATH:fan_system | demand_control_ventilation_control |  |  | FanSystem | Fan System 1 | HVAC 1 | demand_control_ventilation_control | [32 empty] | CO2_ZONE | NONE
rmr_transformations | baseline | JSON_PATH:boilers[0] | id
rmr_transformations | baseline | JSON_PATH:boilers[0] | loop
rmr_transformations | baseline | JSON_PATH:boilers[0] | energy_source_type
rmr_transformations | baseline | JSON_PATH:chillers[0] | id
rmr_transformations | baseline | JSON_PATH:chillers[0] | cooling_loop
rmr_transformations | baseline | JSON_PATH:chillers[0] | design_capacity
rmr_transformations | baseline | JSON_PATH:chillers[0] | energy_source_type
rmr_transformations | baseline | JSON_PATH:chillers[0] | full_load_efficiency
rmr_transformations | baseline | JSON_PATH:chillers[0] | compressor_type
rmr_transformations | baseline | JSON_PATH:chillers[1] | id
rmr_transformations | baseline | JSON_PATH:chillers[1] | cooling_loop
rmr_transformations | baseline | JSON_PATH:chillers[1] | design_capacity
rmr_transformations | baseline | JSON_PATH:chillers[2] | id
rmr_transformations | baseline | JSON_PATH:chillers[2] | cooling_loop
rmr_transformations | baseline | JSON_PATH:chillers[2] | design_capacity
rmr_transformations | baseline | JSON_PATH:chillers[3] | id
rmr_transformations | baseline | JSON_PATH:chillers[3] | cooling_loop
rmr_transformations | baseline | JSON_PATH:chillers[3] | design_capacity
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | id
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | loop
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | type
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature | [6 empty] | temperature | F
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | design_water_flowrate
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature | [6 empty] | temperature | F
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | fan_speed_control
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | range
rmr_transformations | baseline | JSON_PATH:heat_rejections[0] | reset_type
rmr_transformations | baseline | JSON_PATH:heat_rejections[1] | id
rmr_transformations | baseline | JSON_PATH:heat_rejections[1] | loop
rmr_transformations | baseline | JSON_PATH:heat_rejections[1] | type
rmr_transformations | baseline | JSON_PATH:pumps[0] | id
rmr_transformations | baseline | JSON_PATH:pumps[0] | loop_or_piping
rmr_transformations | baseline | JSON_PATH:pumps[0] | speed_control
rmr_transformations | baseline | JSON_PATH:pumps[0] | design_electric_power
rmr_transformations | baseline | JSON_PATH:pumps[0] | design_flow
rmr_transformations | baseline | JSON_PATH:pumps[0] | design_head
rmr_transformations | baseline | JSON_PATH:pumps[0] | motor_efficiency
rmr_transformations | baseline | JSON_PATH:pumps[0] | impeller_efficiency
rmr_transformations | baseline | JSON_PATH:pumps[1] | id
rmr_transformations | baseline | JSON_PATH:pumps[1] | loop_or_piping
rmr_transformations | baseline | JSON_PATH:pumps[1] | speed_control
rmr_transformations | baseline | JSON_PATH:pumps[1] | design_electric_power
rmr_transformations | baseline | JSON_PATH:pumps[1] | design_flow
rmr_transformations | baseline | JSON_PATH:pumps[2] | id
rmr_transformations | baseline | JSON_PATH:pumps[2] | loop_or_piping
rmr_transformations | baseline | JSON_PATH:pumps[2] | speed_control
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id | [51 empty] | CCD 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature | [5 empty] | temperature | F
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature | [5 empty] | temperature | F
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | has_integrated_waterside_economizer | [51 empty] | true
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | child_loops[0] | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | child_loops[0] | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | child_loops[0] | id
rmr_transformations | baseline | JSON_PATH:output | id |  |  | Output | Output 1 | ASHRAE229 1 | id | [17 empty] | Output 1 | Output 1 | Output 1 | Output 1
rmr_transformations | baseline | JSON_PATH:output | output_instance | id |  | Output | Output 1 | OutputInstance | id | [17 empty] | Output Instance 1 | Output Instance 1 | Output Instance 1 | Output Instance 1
rmr_transformations | baseline | JSON_PATH:output | output_instance | unmet_load_hours_heating |  | Output | Output 1 | OutputInstance | unmet_load_hours_heating | [17 empty] | 0 | 50 | 400 | 200
rmr_transformations | baseline | JSON_PATH:output | output_instance | unmet_load_hours_cooling |  | Output | Output 1 | OutputInstance | unmet_load_hours_cooling | [17 empty] | 0 | 100 | 400 | 500
rmr_transformations | baseline | JSON_PATH:output | output_instance | unmet_load_hours |  | Output | Output 1 | OutputInstance | unmet_load_hours | [17 empty] | 200 | 350 | 350 | 350
rmr_transformations | baseline | JSON_PATH:output | output_instance | unmet_occupied_load_hours_heating |  | Output | Output 1 | OutputInstance | unmet_occupied_load_hours_heating | [17 empty] | 0 | 0 | 0 | 0
rmr_transformations | baseline | JSON_PATH:output | output_instance | unmet_occupied_load_hours_cooling |  | Output | Output 1 | OutputInstance | unmet_occupied_load_hours_cooling | [17 empty] | 0 | 0 | 0 | 0
rmr_transformations | baseline | JSON_PATH:output | output_instance | building_peak_cooling_load |  | Output | Output 1 | OutputInstance | building_peak_cooling_load | cooling_capacity | ton | [15 empty] | 200 | 200 | 200 | 200
rmr_transformations | baseline | JSON_PATH:fan_system | air_economizer | id |  | Air Economizer | Air Economizer 1 | HVAC 1 | id | [35 empty] | Air Economizer 1 | Air Economizer 1 | Air Economizer 1 |  |  | Air Economizer 1 |  |  |  |  | Air Economizer 1 |  |  |  | Air Economizer 1 | Air Economizer 1 | Air Economizer 1 |  | Air Economizer 1
rmr_transformations | baseline | JSON_PATH:fan_system | air_economizer | type |  | Air Economizer | Air Economizer 1 | HVAC 1 | type | [35 empty] | FIXED_FRACTION | ENTHALPY | ENTHALPY |  |  | ENTHALPY |  |  |  |  | ENTHALPY |  |  |  | TEMPERATURE | TEMPERATURE | ENTHALPY |  | TEMPERATURE
rmr_transformations | baseline | JSON_PATH:fan_system | air_economizer | high_limit_shutoff_temperature |  | Air Economizer | Air Economizer 1 | HVAC 1 | high_limit_shutoff_temperature | temperature | F | [47 empty] | 75 | 100 | 75 |  | 75
rmr_transformations | baseline | JSON_PATH:fan_system | air_energy_recovery | id |  | Air Energy Recovery | Air Energy Recovery 1 | HVAC 1 | id | [82 empty] | Air Energy Recovery 1 | [10 empty] | Air Energy Recovery 1 | Air Energy Recovery 1 | [27 empty] | Air Energy Recovery 1
rmr_transformations | baseline | JSON_PATH:fan_system | air_energy_recovery | energy_recovery_operation |  | Air Energy Recovery | Air Energy Recovery 1 | HVAC 1 | energy_recovery_operation | [82 empty] | WHEN_MINIMUM_OUTSIDE_AIR | [10 empty] | WHEN_MINIMUM_OUTSIDE_AIR | WHEN_FANS_ON
rmr_transformations | baseline | JSON_PATH:fan_system | air_energy_recovery | outdoor_airflow |  | Air Energy Recovery | Air Energy Recovery 1 | HVAC 1 | outdoor_airflow | air_flow_rate | cfm | [120 empty] | 10000
rmr_transformations | baseline | JSON_PATH:fan_system | air_energy_recovery | design_sensible_effectiveness |  | Air Energy Recovery | Air Energy Recovery 1 | HVAC 1 | design_sensible_effectiveness | [122 empty] | 0.5
rmr_transformations | baseline | JSON_PATH:fan_system | air_energy_recovery | design_latent_effectiveness |  | Air Energy Recovery | Air Energy Recovery 1 | HVAC 1 | design_latent_effectiveness | [122 empty] | 0.5
rmr_transformations | baseline | JSON_PATH:fan_system | air_energy_recovery | exhaust_airflow |  | Air Energy Recovery | Air Energy Recovery 1 | HVAC 1 | exhaust_airflow | air_flow_rate | cfm | [120 empty] | 10000
rmr_transformations | baseline | JSON_PATH:fan_system | air_energy_recovery | enthalpy_recovery_ratio |  | Air Energy Recovery | Air Energy Recovery 1 | HVAC 1 | enthalpy_recovery_ratio | [122 empty] | 0.5
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id | [80 empty] | Supply fan 1 | Supply fan 1
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[0] | specification_method |  | Fan | Supply Fan 1 | HVAC 1 | specification_method | [54 empty] | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE |  |  |  | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[0] | design_electric_power |  | Fan | Supply Fan 1 | HVAC 1 | design_electric_power | electric_power | W | [52 empty] | 3000 | 3000 | 3000 | 3000 | 600 | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 75 | 90 | 75 | 75 |  |  |  | 59 | 56 | 80 | 59 | 80 | 60 | 60 | 120 | 60
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[0] | design_airflow |  | Fan | Supply Fan 1 | HVAC 1 | design_airflow | air_flow_rate | cfm | [52 empty] | 5000 | 5000 | 5000 | 5000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 250 | 250 | 300 | 250 | 250 |  |  |  | 1000 | 1000 | 800 | 1000 | 800 | 1000 | 1000 | 1000 | 1000 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | 5100 | [25 empty] | 5000 | 5000 | 5000 | 5000 | 10000
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[0] | is_airflow_autosized | [59 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | [6 empty] | TRUE | TRUE | TRUE | TRUE | TRUE
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id | [73 empty] | Return fan 1 | Return fan 1 | Return fan 1 | Return fan 1 | Return fan 1 | Return fan 1 | Return fan 1 | Return fan 1 | Return fan 1
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[0] | specification_method |  | Fan | Return Fan 1 | HVAC 1 | specification_method | [54 empty] | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE |  |  |  | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[0] | design_electric_power |  | Fan | Return Fan 1 | HVAC 1 | design_electric_power | electric_power | W | [52 empty] | 2250 | 2250 | 2250 | 2250 | 450 | 0 | 90 | 90 | 92 | 85 | 30 | 25 | 25 | 25 | 25 | 25 |  |  |  | 59 | 56 | 80 | 59 | 80 | 60 | 60 | 60 | 60
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[0] | design_airflow |  | Fan | Return Fan 1 | HVAC 1 | design_airflow | air_flow_rate | cfm | [52 empty] | 4500 | 4500 | 4500 | 4500 | 900 | 0 | 900 | 900 | 950 | 800 | 100 | [15 empty] | 800 | 800 | [40 empty] | 10000
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[0] | is_airflow_autosized | [59 empty] | TRUE | TRUE | TRUE | TRUE | TRUE
rmr_transformations | baseline | JSON_PATH:fan_system | relief_fans[0] | id |  | Fan | Relief Fan 1 | HVAC 1 | id | [73 empty] | Relief fan 1 | Relief fan 1 | Relief fan 1 | Relief fan 1 | Relief fan 1 | Relief fan 1 | Relief fan 1 | Relief fan 1 | Relief fan 1
rmr_transformations | baseline | JSON_PATH:fan_system | relief_fans[0] | specification_method |  | Fan | Relief Fan 1 | HVAC 1 | specification_method | [73 empty] | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE
rmr_transformations | baseline | JSON_PATH:fan_system | relief_fans[0] | design_electric_power |  | Fan | Relief Fan 1 | HVAC 1 | design_electric_power | electric_power | W | [71 empty] | 59 | 56 | 80 | 59 | 80 | 60 | 60 | 0 | 60
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[1] | id |  | Fan | Relief Fan 2 | HVAC 1 | id | [64 empty] | Return Fan 2
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[1] | specification_method | [69 empty] | SIMPLE
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[1] | design_electric_power | [5 empty] | electric_power | W | [62 empty] | 30
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[1] | design_airflow | [5 empty] | air_flow_rate | cfm | [62 empty] | 100
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[0] | id |  | Fan | Exhaust Fan 1 | HVAC 1 | id | [73 empty] | Exhaust fan 1 | Exhaust fan 1 | Exhaust fan 1 | Exhaust fan 1 | Exhaust fan 1 | Exhaust fan 1 | Exhaust fan 1 | Exhaust fan 1 | Exhaust fan 1 | [7 empty] | Exhaust Fan 1
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[0] | specification_method |  | Fan | Exhaust Fan 1 | HVAC 1 | specification_method | [73 empty] | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | SIMPLE | [7 empty] | SIMPLE
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[0] | design_electric_power |  | Fan | Exhaust Fan 1 | HVAC 1 | design_electric_power | electric_power | W | [71 empty] | 59 | 56 | 80 | 59 | 80 | 60 | 60 | 60 | 60
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[0] | design_airflow | [5 empty] | air_flow_rate | cfm | [87 empty] | 2500
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[1] | id | [94 empty] | Exhaust Fan 2
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[1] | specification_method | [94 empty] | SIMPLE
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[1] | design_electric_power
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[1] | design_airflow | [94 empty] | 2500
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[1] | id |  | Fan | Relief Fan 2 | HVAC 1 | id | [69 empty] | Supply Fan 2 | [8 empty] | Supply Fan 2
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[1] | specification_method | [74 empty] | SIMPLE | [8 empty] | SIMPLE
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[1] | design_electric_power | [5 empty] | electric_power | W | [67 empty] | 75 | [8 empty] | 360
rmr_transformations | baseline | JSON_PATH:fan_system | supply_fans[1] | design_airflow | [5 empty] | air_flow_rate | cfm | [67 empty] | 250 | [8 empty] | 1200
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[1] | id |  | Fan | Relief Fan 2 | HVAC 1 | id | [64 empty] | Return Fan 2
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[1] | specification_method | [69 empty] | SIMPLE
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[1] | design_electric_power | [5 empty] | electric_power | W | [62 empty] | 30
rmr_transformations | baseline | JSON_PATH:fan_system | return_fans[1] | design_airflow | [5 empty] | air_flow_rate | cfm | [62 empty] | 100
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[1] | id
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[1] | specification_method
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[1] | design_electric_power | [5 empty] | electric_power | W
rmr_transformations | baseline | JSON_PATH:fan_system | exhaust_fans[1] | design_airflow | [5 empty] | air_flow_rate | cfm
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | id |  | HeatingDesignControl | Boiler Loop HDC 1 | FluidLoop 1 | id | [7 empty] | Boiler Loop HDC 1 | Boiler Loop HDC 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load |  | HeatingDesignControl | Boiler Loop HDC 1 | FluidLoop 1 | is_sized_using_coincident_load | [7 empty] | TRUE | FALSE
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | cooling_or_condensing_design_and_control | id |  | CoolingCondensingDesignControl | Chilled Water Loop HDC 1 | FluidLoop 2 | id | [7 empty] | Chilled Water Loop HDC 1 | Chilled Water Loop HDC 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | cooling_or_condensing_design_and_control | is_sized_using_coincident_load |  | CoolingCondensingDesignControl | Chilled Water Loop HDC 1 | FluidLoop 2 | is_sized_using_coincident_load | [7 empty] | TRUE | FALSE
rmr_transformations | baseline | JSON_PATH:schedules[0] | id |  |  | Schedule | Schedule 1 | RMR 1 | id | [9 empty] | Infiltration Schedule 1 | Infiltration Schedule 1 | Infiltration Schedule 1 | Infiltration Schedule 1 | [8 empty] | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | Outdoor Airflow Multiplier Schedule 1 | [50 empty] | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | Heating Temperature Setpoint Schedule 1 | [25 empty] | Min OA CFM Schedule | Min OA CFM Schedule | Min OA CFM Schedule | Min OA CFM Schedule
rmr_transformations | baseline | JSON_PATH:schedules[0] | hourly_values |  |  | Schedule | Schedule 1 | RMR 1 | hourly_values | [9 empty] | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | [8 empty] | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-0.93 | SCHEDULE:CONSTANT-1.0 | [50 empty] | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-13 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | SCHEDULE:CONSTANT-21 | [25 empty] | SCHEDULE:CONSTANT-2360 | SCHEDULE:CONSTANT-2360 | SCHEDULE:CONSTANT-2360 | SCHEDULE:CONSTANT-2360
rmr_transformations | baseline | JSON_PATH:schedules[0] | hourly_cooling_design_day | [15 empty] | SCHEDULE:CONSTANT_DAY-1.0 | SCHEDULE:CONSTANT_DAY-0.0 | SCHEDULE:CONSTANT_DAY-1.0 | SCHEDULE:CONSTANT_DAY-1.0
rmr_transformations | baseline | JSON_PATH:schedules[0] | type | [88 empty] | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | TEMPERATURE | [25 empty] | FLOW_RATE | FLOW_RATE | FLOW_RATE | FLOW_RATE
rmr_transformations | baseline | JSON_PATH:schedules[1] | id |  |  | Schedule | Schedule 2 | RMR 1 | id | [9 empty] | Occupancy Schedule 1 | Occupancy Schedule 1 | Occupancy Schedule 1 | Occupancy Schedule 1
rmr_transformations | baseline | JSON_PATH:schedules[1] | hourly_values |  |  | Schedule | Schedule 2 | RMR 1 | hourly_values | [9 empty] | SCHEDULE:CONSTANT-1.0 | SCHEDULE:LIBRARY-Office_Occupancy | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0
rmr_transformations | baseline | JSON_PATH:schedules[1] | hourly_cooling_design_day | [15 empty] | SCHEDULE:CONSTANT_DAY-1.0 | SCHEDULE:CONSTANT_DAY-0.0 | SCHEDULE:CONSTANT_DAY-1.0 | SCHEDULE:CONSTANT_DAY-1.0
rmr_transformations | baseline | JSON_PATH:schedules[2] | id |  |  | Schedule | Schedule 3 | RMR 1 | id | [9 empty] | Lighting Schedule 1 | Lighting Schedule 1 | Lighting Schedule 1 | Lighting Schedule 1
rmr_transformations | baseline | JSON_PATH:schedules[2] | hourly_values |  |  | Schedule | Schedule 3 | RMR 1 | hourly_values | [9 empty] | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0
rmr_transformations | baseline | JSON_PATH:schedules[2] | hourly_cooling_design_day | [15 empty] | SCHEDULE:CONSTANT_DAY-1.0 | SCHEDULE:CONSTANT_DAY-0.0 | SCHEDULE:CONSTANT_DAY-1.0 | SCHEDULE:CONSTANT_DAY-1.0
rmr_transformations | baseline | JSON_PATH:schedules[3] | id |  |  | Schedule | Schedule 4 | RMR 1 | id | [9 empty] | Misc Schedule 1 | Misc Schedule 1 | Misc Schedule 1 | Misc Schedule 1
rmr_transformations | baseline | JSON_PATH:schedules[3] | hourly_values |  |  | Schedule | Schedule 4 | RMR 1 | hourly_values | [9 empty] | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0 | SCHEDULE:CONSTANT-1.0
rmr_transformations | baseline | JSON_PATH:schedules[3] | hourly_cooling_design_day | [15 empty] | SCHEDULE:CONSTANT_DAY-1.0 | SCHEDULE:CONSTANT_DAY-0.0 | SCHEDULE:CONSTANT_DAY-1.0 | SCHEDULE:CONSTANT_DAY-1.0
rmr_transformations | baseline | JSON_PATH:schedules[4] | id
rmr_transformations | baseline | JSON_PATH:schedules[4] | hourly_values
Note on ED1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should be double-checked after the schema is updated.
Note on EQ1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The pass case isn't modeled because we only have system type 7 and 11.1 for now. When we have more system types, the pass case will be modeled. Reply: Hi Yun Joon, I added a lot of systems to the templates so that we could properly model these. Reply: Thanks Juan! I updated this rule.

## Lookups
test_outcome_types | true/false | yes/no | applicable_rmr | rule_assertions | comparison_rmr
pass | true | Yes | User RMR | = | Expected Value
fail | false | No | Proposed RMR | <= | User RMR
undetermined |  |  | Baseline RMR | >= | Proposed RMR
not_applicable |  |  |  |  | Baseline RMR

## Templates_old (hidden)
key1 | key2 | key3 | key4 | data_group | object_id | parent_id | data_element | unit_type | units | System_7_VAV_HW_Reheat | System_7a_VAV_HW_Reheat | System_11.1_VAV_SZ | PurchasedWater | rule-22-1-a | rule-22-1-b | rule-22-2-a | rule-22-2-b | rule-22-3-a | rule-22-3-b | rule-22-4-a | rule-22-4-b | rule-22-4-c | rule-22-4-d | rule-22-4-e | rule-22-5-a | rule-22-5-b | rule-22-6-a | rule-22-6-b | rule-22-7-a | rule-22-7-b | rule-22-7-c | rule-22-8-a | rule-22-8-b | rule-22-8-c | rule-22-8-d | rule-22-9-a | rule-22-9-b | rule-22-10-a | rule-22-10-b | rule-22-10-c | rule-22-11-a | rule-22-11-b | rule-18-1-a | rule-18-1-b | rule-18-2-a | rule-18-2-b | rule-18-3-a | rule-18-3-b | rule-18-4-a | rule-18-4-b | rule-18-5-a | rule-18-5-b | rule-22-12-a | rule-22-12-b | rule-22-12-c | rule-22-13-a | rule-22-13-b | rule-22-14-a | rule-22-14-b | rule-22-15-a | rule-22-15-b | rule-22-15-c | rule-22-16-a | rule-22-16-b | rule-22-17-a | rule-22-17-b | rule-22-18-a | rule-22-18-b | rule-22-19-a | rule-22-19-b | rule-22-20-a | rule-22-20-b | rule-22-21-a | rule-22-21-b | rule-22-21-c | rule-22-21-d | rule-22-21-e | rule-22-22-a | rule-22-22-b | rule-22-22-c | rule-22-22-d | rule-22-23-a | rule-22-23-b | rule-22-23-c | rule-22-23-d | rule-22-23-e | rule-22-23-f | rule-22-24-a | rule-22-24-b | rule-22-24-c | rule-22-25-a | rule-22-25-b | rule-22-26-a | rule-22-26-b | rule-22-27-a | rule-22-27-b | rule-22-28-a | rule-22-28-b | rule-22-28-c | rule-22-28-d | rule-22-29-a | rule-22-29-b | rule-22-30-a | rule-22-30-b | rule-22-31-a | rule-22-31-b | rule-22-32-a | rule-22-32-b | rule-22-32-c | rule-22-32-d | rule-22-32-e | rule-22-32-f | rule-22-32-g | rule-22-32-h
id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | TODO | TODO | TODO | TODO | TODO | TODO | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
weather | climate_zone |  |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone |  |  | CZ4A | CZ4A | [61 empty] | CZ5C | CZ3C | CZ4A | CZ1A | CZ5C
ruleset_model_instances[0] | id |  |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1
JSON_PATH:buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | [11 empty] | Building 1 | Building 1 | Building 1 | Building 1 | [66 empty] | Building 1 | Building 1
JSON_PATH:buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | [11 empty] | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | [66 empty] | Required Building Schedule 1 | Required Building Schedule 1
JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | [11 empty] | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | [66 empty] | Building Segment 1 | Building Segment 1
JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | [11 empty] | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | [66 empty] | Thermal Zone 1 | Thermal Zone 1
JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [11 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | [66 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1
JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | [11 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | [66 empty] | Required Heating Schedule 1 | Required Heating Schedule 1
JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Terminal 1 | [11 empty] | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | [66 empty] | VAV Air Terminal 1 | VAV Air Terminal 1
JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | true | true | true | false | [11 empty] | true | true | true | true | [66 empty] | true | true
JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | HOT_WATER | HOT_WATER | [13 empty] | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | [66 empty] | HOT_WATER | HOT_WATER
JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [12 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | [66 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME
JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilation_air_conditioning_system |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilation_air_conditioning_systems |  |  | VAV System 1 | VAV System 1 | System 11 | AHU_HW_System1 | [11 empty] | VAV System 1 | VAV System 1 | VAV System 1 | VAV System 1 | [66 empty] | VAV System 1 | VAV System 1
JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | HOT_WATER | HOT_WATER
JSON_PATH:zones[0] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  | Boiler Loop 1 | Boiler Loop 1
JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id |  |  | Thermal Zone 2 | Thermal Zone 2 |  | Thermal Zone 2
JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 |  | Required Cooling Schedule 1
JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 |  | Required Heating Schedule 1
JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id |  |  | VAV Air Terminal 2 | VAV Air Terminal 2 |  | Terminal 1
JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  | true | true |  | false
JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | HOT_WATER | HOT_WATER
JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type |  |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME
JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilation_air_conditioning_system |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilation_air_conditioning_systems |  |  | System 7 | System 7 |  | AHU_HW_System1
JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | HOT_WATER | HOT_WATER
JSON_PATH:zones[1] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop |  |  | Boiler Loop 1 | Boiler Loop 1
JSON_PATH:heating_ventilation_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | System 7 | System 7 | System 11 | AHU_HW_System1 | [11 empty] | System Type 11 | System Type 11 | System Type 11 | System Type 11 | [66 empty] | System Type 11 | System Type 11
JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | [12 empty] | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | [66 empty] | CHW Coil 1 | CHW Coil 1
JSON_PATH:cooling_system | cooling_system_type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | [12 empty] | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | [66 empty] | FLUID_LOOP | FLUID_LOOP
JSON_PATH:cooling_system | chilled_water_loop |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1
JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  |  |  | Heating Coil 1 | HHW Coil 1 | [11 empty] | HHW Coil 1 | HHW Coil 1 | HHW Coil 1 | HHW Coil 1 | [66 empty] | HHW Coil 1 | HHW Coil 1
JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  |  |  | ELECTRIC_RESISTANCE | FLUID_LOOP | [11 empty] | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | [66 empty] | FLUID_LOOP | FLUID_LOOP
JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop | [17 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [66 empty] | Boiler Loop 1 | Boiler Loop 1
JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | [12 empty] | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | [66 empty] | VAV Fan System 1 | VAV Fan System 1
JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | [12 empty] | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | [66 empty] | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE
JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | [12 empty] | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | [66 empty] | Supply Fan 1 | Supply Fan 1
JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | [12 empty] | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | [66 empty] | Return Fan 1 | Return Fan 1
JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1 | Boiler 1 | [13 empty] | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | [66 empty] | Boiler 1 | Boiler 1
JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | Boiler Loop 1 | Boiler Loop 1 | [13 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | [66 empty] | Boiler Loop 1 | Boiler Loop 1
JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | NATURAL_GAS | NATURAL_GAS | [13 empty] | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | [66 empty] | NATURAL_GAS | NATURAL_GAS
JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id |  |  | Chiller 1 |  | Chiller 1 | [12 empty] | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 |  |  |  | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 |  |  | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 |  |  | Chilled Water 1 | Chilled Water 1 | [31 empty] | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1
JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop |  |  | Chiller Loop 1 |  | Chiller Loop 1 | [12 empty] | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 |  |  | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 |  |  | Chilled Water Loop 1 | Chilled Water Loop 1 | [31 empty] | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1
JSON_PATH:chillers[0] | design_capacity |  |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton | [22 empty] | 400 | 300 | 400 | 250 |  |  | 250 | 250 | 250 | [37 empty] | 599 | 600 | 550 | 700 | 149 | 299 | 300 | 300 | 299 | 149 | [19 empty] | 300 | 300 | 300 | 800 | 800 | 600 | 500 | 900
JSON_PATH:chillers[0] | energy_source_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type | [17 empty] | ELECTRICITY | ELECTRICITY | ELECTRICITY | ELECTRICITY | [66 empty] | ELECTRICITY | ELECTRICITY
JSON_PATH:chillers[0] | full_load_efficiency |  |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton | [72 empty] | 0.79 | 0.718 | 0.526 | 0.718 | 0.576 | 0.676
JSON_PATH:chillers[0] | compressor_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type | [70 empty] | SCREW | CENTRIFUGAL | CENTRIFUGAL | SCREW | SCREW | SCREW | CENTRIFUGAL | CENTRIFUGAL | SCREW | SCREW
JSON_PATH:chillers[1] | id |  |  | Chiller | Chiller 2 | ASHRAE229 1 | id | [100 empty] | Chiller 2 | Chiller 2 | Chiller 2 | Chiller 2 |  | Chiller 2
JSON_PATH:chillers[1] | cooling_loop |  |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop | [100 empty] | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1
JSON_PATH:chillers[1] | design_capacity |  |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton | [98 empty] | 300 | 300 | 800 | 800 |  | 500
JSON_PATH:chillers[2] | id |  |  | Chiller | Chiller 3 | ASHRAE229 1 | id | [102 empty] | Chiller 3 | Chiller 3 |  | Chiller 3
JSON_PATH:chillers[2] | cooling_loop |  |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop | [102 empty] | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1
JSON_PATH:chillers[2] | design_capacity |  |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton | [100 empty] | 800 | 800 |  | 500
JSON_PATH:chillers[3] | id |  |  | Chiller | Chiller 4 | ASHRAE229 1 | id | [103 empty] | Chiller 4 |  | Chiller 4
JSON_PATH:chillers[3] | cooling_loop |  |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop | [103 empty] | Chiller Loop 1 |  | Chiller Loop 1
JSON_PATH:chillers[3] | design_capacity |  |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton | [101 empty] | 800 |  | 500
JSON_PATH:heat_rejections[0] | id |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id | [45 empty] | Cooling Tower 1 |  | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | [9 empty] | Cooling Tower 1 | Cooling Tower 1 |  |  | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1 | Cooling Tower 1
JSON_PATH:heat_rejections[0] | loop |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop | [45 empty] | Condensing Water Loop 1 |  | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | [9 empty] | Condensing Water Loop 1 | Condensing Water Loop 1 |  |  | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1
JSON_PATH:heat_rejections[0] | type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type | [45 empty] | OPEN_CIRCUIT_COOLING_TOWER |  | OPEN_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | DRY_COOLER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER | CLOSED_CIRCUIT_COOLING_TOWER
JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F | [55 empty] | 85 | 83
JSON_PATH:heat_rejections[0] | design_water_flowrate |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min | [57 empty] | 51 | 40
JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F | [50 empty] | 75 | 52 | 92 | 73.4 | 73.4 | 73.4 | 73.4
JSON_PATH:heat_rejections[0] | fan_power |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_power | electric_power | W | [57 empty] | 1000 | 1000
JSON_PATH:heat_rejections[0] | fan_speed_control |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control | [61 empty] | VARIABLE_SPEED | TWO_SPEED
JSON_PATH:heat_rejections[0] | range |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature_difference | R | [48 empty] | 42 | 40 |  |  |  | 42 | 40
JSON_PATH:heat_rejections[0] | reset_type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type | [63 empty] | LOAD_RESET | OTHER
JSON_PATH:heat_rejections[0] | minimum_reset_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | minimum_reset_temperature | [65 empty] | 65 | 70 | 75 | 80 | 80
JSON_PATH:heat_rejections[1] | id |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id | [47 empty] | Cooling Tower 2
JSON_PATH:heat_rejections[1] | loop |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | loop | [47 empty] | Condensing Water Loop 1
JSON_PATH:heat_rejections[1] | type |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | type | [47 empty] | OPEN_CIRCUIT_COOLING_TOWER
JSON_PATH:external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id |  |  |  | Purchased CW 1 |  | Purchased HW 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 |  |  |  |  | Chilled Water 1 | Chilled Water 1 | Chilled Water 1 | [11 empty] | Chilled Water 1 | Chilled Water 1
JSON_PATH:external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop |  |  |  | Chilled Water Loop 1 |  | Purchased HW Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 |  |  |  |  | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | [11 empty] | Chilled Water Loop 1 | Chilled Water Loop 1
JSON_PATH:external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type |  |  |  | CHILLED_WATER |  | HOT_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER |  |  |  |  | CHILLED_WATER | CHILLED_WATER | CHILLED_WATER | [11 empty] | CHILLED_WATER | CHILLED_WATER
JSON_PATH:pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id |  |  | Boiler Pump 1 | Boiler Pump 1 | Chiller Pump 1 | [12 empty] | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 |  |  | Primary Pump 1 | Primary Pump 1 | [41 empty] | Primary Pump 1 |  | Secondary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Primary Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Condensing Water Pump 1 | Chiller Pump 1 |  |  | Condensing Water Pump 1 | Condensing Water Pump 1 | Condensing Water Pump 1 | Condensing Water Pump 1 | Chiller Pump 1 | Chiller Pump 1
JSON_PATH:pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping |  |  | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 | [12 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  | Chiller Loop 1 | Chiller Loop 1 | [41 empty] | Chiller Loop 1 |  | Secondary Water Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Condensing Water Loop 1 | Chiller Loop 1 |  |  | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Chiller Loop 1 | Chiller Loop 1
JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | [12 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED | [44 empty] | FIXED_SPEED | VARIABLE_SPEED |  |  | FIXED_SPEED | FIXED_SPEED |  |  |  |  | FIXED_SPEED | VARIABLE_SPEED
JSON_PATH:pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W | [83 empty] | 900 | 1000 | [8 empty] | 1900 | 2200 | 2200 | 2000
JSON_PATH:pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min | [83 empty] | 100 | 100 | [8 empty] | 100 | 100 | 100 | 100
JSON_PATH:pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
JSON_PATH:pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
JSON_PATH:pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
JSON_PATH:pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id |  |  | Chiller Pump 1 | CHW Pump 1 | [13 empty] | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Secondary Pump 1 | Primary Pump 2 |  | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 | Secondary Pump 1 |  |  | Secondary Pump 1 | Secondary Pump 1 | [48 empty] | Chiller Pump 1 | Chiller Pump 1
JSON_PATH:pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping |  |  | Chiller Loop 1 | Chilled Water Loop 1 | [13 empty] | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Secondary Water Loop 1 | Chiller Loop 1 |  | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 |  |  | Secondary Water Loop 1 | Secondary Water Loop 1 | [48 empty] | Chiller Loop 1 | Chiller Loop 1
JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control |  |  | FIXED_SPEED | FIXED_SPEED | [13 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  | VARIABLE_SPEED | VARIABLE_SPEED |  | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | FIXED_SPEED | VARIABLE_SPEED | VARIABLE_SPEED |  |  | VARIABLE_SPEED | VARIABLE_SPEED | [48 empty] | FIXED_SPEED | FIXED_SPEED
JSON_PATH:pumps[1] | design_electric_power |  |  | Pump | Pump 2 | ASHRAE229 1 | design_electric_power | electric_power | W | [31 empty] | 1300 | 1500 | [52 empty] | 1200 | 1400
JSON_PATH:pumps[1] | design_flow |  |  | Pump | Pump 2 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min | [31 empty] | 100 | 100 | [52 empty] | 100 | 100
JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id
JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping
JSON_PATH:fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id |  |  | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Purchased HW Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | [6 empty] | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1
JSON_PATH:fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type |  |  | HEATING | HEATING | COOLING | HEATING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | [6 empty] | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING |  |  |  |  | HEATING | HEATING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id | [6 empty] | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | Cool DAC 1 | [14 empty] | Cool DAC 1 | Cool DAC 1
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F |  |  |  |  | 44 | 41
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F | [6 empty] | 56 | 50
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type | [10 empty] | OUTSIDE_AIR_RESET | NO_RESET | OUTSIDE_AIR_RESET | OUTSIDE_AIR_RESET | OUTSIDE_AIR_RESET | OUTSIDE_AIR_RESET | OUTSIDE_AIR_RESET | LOAD_RESET | NO_RESET | [16 empty] | NO_RESET | LOAD_RESET
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | outdoor_high_for_loop_supply_temperature_reset |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_high_for_loop_supply_temperature_reset | temperature | F | [17 empty] | 54 | 50
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | outdoor_low_for_loop_supply_temperature_reset |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_low_for_loop_supply_temperature_reset | temperature | F
JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 1 | id | [21 empty] | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 | Secondary Water Loop 1 |  |  | Secondary Water Loop 1 | Secondary Water Loop 1 | [31 empty] | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 |  |  | Secondary Water Loop 1 | [6 empty] | Condensing Water Loop 1 | Condensing Water Loop 1 |  |  | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1
JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 1 | type | [21 empty] | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING |  |  | COOLING | COOLING | [31 empty] | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER |  |  | COOLING | [6 empty] | CONDENSER | CONDENSER |  |  | CONDENSER | CONDENSER | CONDENSER | CONDENSER
JSON_PATH:fluid_loops[0] | child_loops[0] | cooling_or_condensing_design_and_control | id | [32 empty] | Cool DAC 1 | Cool DAC 1
JSON_PATH:fluid_loops[0] | child_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction | FluidLoopDesignAndControl | DAC 2 | SecondaryLoop 1 | minimum_flow_fraction | [28 empty] | 0.25 | 0.4
JSON_PATH:fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id |  |  | Chiller Loop 1 | [14 empty] | HEATING | HEATING | HEATING | HEATING | [66 empty] | Chiller Loop 1 | Chiller Loop 1
JSON_PATH:fluid_loops[1] | type |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | type |  |  | COOLING | [84 empty] | COOLING | COOLING
JSON_PATH:preheat_system | id |  |  | PreheatSystem | Heating System 1 | HVAC 1 | id |  |  | Preheat Coil 1
JSON_PATH:preheat_system | heating_system_type |  |  | PreheatSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  | FLUID_LOOP
JSON_PATH:preheat_system | hot_water_loop |  |  | PreheatSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | Boiler Loop 1
JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | VAV Fan System 1
JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | VARIABLE_SPEED_DRIVE
JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1
JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1
JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1
JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | Boiler Loop 1
JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | NATURAL_GAS
JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id |  |  | Chiller 1
JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop |  |  | Chiller Loop 1
Note on U1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Per the TCD spreadsheet, "These tests are not finished. Need to figure out best way to test schedule"
Note on AN1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TCD has this identical to 22-10-a passing case. Not sure what should be different
Note on AO1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Identical to 22-10-a but context of test description made me change control type to FIXED_SPEED
Note on AT1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Schema does not appear to support distribution pump type? (instead of secondary)
Note on AV1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Schema does not appear to support distribution pump type? (instead of secondary)
Note on AW1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Schema does not appear to support distribution pump type? (instead of secondary)
Note on AX1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Schema does not appear to support distribution pump type? (instead of secondary)
Note on AY1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Schema does not appear to support distribution pump type? (instead of secondary)
Note on AZ1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Schema does not appear to support distribution pump type? (instead of secondary)
Note on BA1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Schema does not appear to support distribution pump type? (instead of secondary)
Note on BP1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated values to agree with rules when converted to IP. TCD seemed off.
Note on CV1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not allowed to have a pump without name. Removing the pump altogether makes this test identical to 28-d
Note on DF1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: identical to B

## TCDs_old (hidden)
key1 | key2 | key3 | key4 | key5 | key6 | data_group | object_id | parent_id | data_element | unit_type | units | rule-22-1-a | rule-22-1-b | rule-22-2-a | rule-22-2-b | rule-22-3-a | rule-22-3-b | rule-22-4-a | rule-22-4-b | rule-22-4-c | rule-22-4-d | rule-22-4-e | rule-22-5-a | rule-22-5-b | rule-22-6-a | rule-22-6-b | rule-22-7-a | rule-22-7-b | rule-22-7-c | rule-22-8-a | rule-22-8-b | rule-22-8-c | rule-22-8-d | rule-22-9-a | rule-22-9-b | rule-22-10-a | rule-22-10-b | rule-22-10-c | rule-22-11-a | rule-22-11-b | rule-18-1-a | rule-18-1-b | rule-18-2-a | rule-18-2-b | rule-18-3-a | rule-18-3-b | rule-18-4-a | rule-18-4-b | rule-18-5-a | rule-18-5-b | rule-22-12-a | rule-22-12-b | rule-22-12-c | rule-22-13-a | rule-22-13-b | rule-22-14-a | rule-22-14-b | rule-22-15-a | rule-22-15-b | rule-22-15-c | rule-22-16-a | rule-22-16-b | rule-22-17-a | rule-22-17-b | rule-22-18-a | rule-22-18-b | rule-22-19-a | rule-22-19-b | rule-22-20-a | rule-22-20-b | rule-22-21-a | rule-22-21-b | rule-22-21-c | rule-22-21-d | rule-22-21-e | rule-22-22-a | rule-22-22-b | rule-22-22-c | rule-22-22-d | rule-22-23-a | rule-22-23-b | rule-22-23-c | rule-22-23-d | rule-22-23-e | rule-22-23-f | rule-22-24-a | rule-22-24-b | rule-22-24-c | rule-22-25-a | rule-22-25-b | rule-22-26-a | rule-22-26-b | rule-22-27-a | rule-22-27-b | rule-22-28-a | rule-22-28-b | rule-22-28-c | rule-22-28-d | rule-22-29-a | rule-22-29-b | rule-22-30-a | rule-22-30-b | rule-22-31-a | rule-22-31-b | rule-22-32-a | rule-22-32-b | rule-22-32-c | rule-22-32-d | rule-22-32-e | rule-22-32-f | rule-22-32-g | rule-22-32-h
Section | [11 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
Rule | [11 empty] | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 6 | 6 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 9 | 9 | 10 | 10 | 10 | 11 | 11 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 12 | 12 | 12 | 13 | 13 | 14 | 14 | 15 | 15 | 15 | 16 | 16 | 17 | 17 | 18 | 18 | 19 | 19 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 25 | 25 | 26 | 26 | 27 | 27 | 28 | 28 | 28 | 28 | 29 | 29 | 30 | 30 | 31 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
Test | [11 empty] | a | b | a | b | a | b | a | b | c | d | e | a | b | a | b | a | b | c | a | b | c | d | a | b | a | b | c | a | b | a | b | a | b | a | b | a | b | a | b | a | b | c | a | b | a | b | a | b | c | a | b | a | b | a | b | a | b | a | b | a | b | c | d | e | a | b | c | d | a | b | c | d | e | f | a | b | c | a | b | a | b | a | b | a | b | c | d | a | b | a | b | a | b | a | b | c | d | e | f | g | h
Notes
test_description | [11 empty] | CHW Loop Supply Temperature equals 44 in Baseline RMR | CHW Loop Supply Temperature does not equal 44 in Baseline RMR | CHW Loop Return Temperature equals 56 in Baseline RMR | CHW Loop Return Temperature does not equal 56 in Baseline RMR | CHW Loop Temperature Reset Type equals "OA Reset" | CHW Loop Temperature Reset Type does not equal "OA Reset" | OA Reset Schedule values are correct | OA Reset Schedule values are not correct | OA Reset Schedule values are not correct | OA Reset Schedule values are not correct | OA Reset Schedule values are not correct | CHW Temperature Rest equals Load Reset when System 11 is used | CHW Temperature Rest does not equal Load Reset when System 11 is used | CHW Loop Maximum Reset Temperature equals 54F | CHW Loop Maximum Reset Temperature does not equal 54F | CHW Loop has an associated secondary pump | CHW Loop does not have an associated secondary pump | CHW Loop does not have an associated secondary pump | Secondary pump speed control equals VFD, design capacity > 300 tons | Secondary pump speed control equals VFD, design capacity =300 tons | Secondary pump speed control does not equal VFD | Secondary pump speed control equals VFD, loop cooling capacity <300 tons | Secondary pump minimum speed setpoint equals 25% when a VFD is used. | Secondary pump minimum speed setpoint does not equal 25% when a VFD is used. | Secondary pump speed control equals "ride curve" | Secondary pump speed control does not equal "ride curve" | Secondary pump speed control equals "ride curve" , loop capacity > 300 tons | Secondary pump power equals 13W per gpm | Secondary pump power does not equal 13W per gpm | Purchasaed CHW Loop temperature reset equals "none" | Purchasaed CHW Loop temperature reset does not equal "none" | Purchased CHW Loop has a distribution pump | Purchased CHW Loop does not have a distribution pump | Distribution Pump speed control equals VFD | Distribution pumps peed control does not equal VFD | Distribution pump minimum speed control equals 25% | Distribution pump minimum speed control does not equal 25% | Distribution pump power equals 16 W per gpm | Distribution pump power does not equal 16W per gpm | Heat rejection loop has a single heat rejection device attached | Heat rejection device has no heat rejection device attached | Heat rejection loop has more than one device attached | Heat rejection Type equals axial fan | Heat rejection type does not equal axial fan | Heat rejection device range equals 10 | Heat rejection device range does not equal 10 | Project location 0.4% MCWB is greater than or equal to 12.8C and less than or equal to 32.2C | Project location 0.4% MCWB is less than 12.8C | Project location 0.4% MCWB is greater than 32.2C | Heat rejection Device Approach is calculated correctly? | Heat rejection Device Approach is not calculated correctly? | Heat Rejection Supply Temperature is calcualted correctly? | Heat Rejection Supply Temperature is not calcualted correctly? | Heat rejection fan power equals 38 gpm per hp? | Heat rejection fan power does not equal 38 gpm per hp? | Heat rejection fan speed control equals VFD | Heat rejection fan speed control does not equal VFD | Heat rejection loop temperature reset equals "load reset" | Heat rejection loop temperature reset does not equal "load reset" | Heat rejection loop minimum reset temperatrue equals Table G3.1.3.11 | Heat rejection loop minimum reset temperatrue does not equal Table G3.1.3.11 | Heat rejection loop minimum reset temperatrue does not equal Table G3.1.3.11 | Heat rejection loop minimum reset temperatrue does not equal Table G3.1.3.11 | Heat rejection loop minimum reset temperatrue does not equal Table G3.1.3.11 | Chiller type is correct per Table G3.1.3.7? | Chiller type is correct per Table G3.1.3.7? | Chiller type is not correct per Table G3.1.3.7? | Chiller type is not correct per Table G3.1.3.7? | Chiller efficiency is correct based on type and capacity | Chiller efficiency is correct based on type and capacity | Chiller efficiency is correct based on type and capacity | Chiller efficiency is not correct based on type and capacity | Chiller efficiency is not correct based on type and capacity | Chiller efficiency is not correct based on type and capacity | Chiller has an associated primary pump | chiller does not have an associated primary pump | chiller does not have an associated primary pump | primary pump speed control equals constant | pimary pump speed control does not equal constant | primary pump power equals 9W per gpm | Primary pump power does not equal 9W per gpm | Primary pump power equals 12W per gpm when loop uses system 11. | Primary pump power does not equal 12W per gpm when loop uses system 11. | chiller has an associated condenser pump | chiller does not have an associated condenser pump of the correct type | chiller does not have an associated condenser pump | chiller associated condenser pump name does not exist as a pump object | condenser pump speed control equals constant | condenser pump speed control does not equal constant | condenser pum power equals 19W per gpm | condenser pump power does not equal 19W per gpm | Distribution pump power equals 22 W per gpm | Distribution pump power does not equal 22W per gpm | CHW Loop has correct number of chillers based on load | CHW Loop has correct number of chillers based on load | CHW Loop has correct number of chillers based on load | CHW Loop has correct number of chillers based on load | CHW Loop has correct number of chillers based on load | CHW loop does not have correct number of chillers based on load | CHW loop does not have correct number of chillers based on load | CHW loop does not have correct number of chillers based on load
expected_rule_outcome | [11 empty] | pass | fail | pass | fail | pass | fail | pass | fail | fail | fail | fail | pass | fail | pass | fail | pass | fail | fail | pass | pass | fail | fail | pass | fail | pass | fail | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | pass | fail | pass | fail | pass | fail | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | fail | fail | fail | pass | pass | fail | fail | pass | pass | pass | fail | fail | pass | pass | fail | fail | pass | fail | pass | fail | pass | fail | pass | fail | fail | fail | pass | fail | pass | fail | pass | fail | pass | pass | pass | pass | pass | fail | fail | fail
standard | rule_id | [10 empty] | 22-1 | 22-1 | 22-2 | 22-2 | 22-3 | 22-3 | 22-4 | 22-4 | 22-4 | 22-4 | 22-4 | 22-5 | 22-5 | 22-6 | 22-6 | 22-7 | 22-7 | 22-7 | 22-8 | 22-8 | 22-8 | 22-8 | 22-9 | 22-9 | 22-10 | 22-10 | 22-10 | 22-11 | 22-11 | 18-1 | 18-1 | 18-2 | 18-2 | 18-3 | 18-3 | 18-4 | 18-4 | 18-5 | 18-5 | 22-12 | 22-12 | 22-12 | 22-13 | 22-13 | 22-14 | 22-14 | 22-15 | 22-15 | 22-15 | 22-16 | 22-16 | 22-17 | 22-17 | 22-18 | 22-18 | 22-19 | 22-19 | 22-20 | 22-20 | 22-21 | 22-21 | 22-21 | 22-21 | 22-21 | 22-22 | 22-22 | 22-22 | 22-22 | 22-23 | 22-23 | 22-23 | 22-23 | 22-23 | 22-23 | 22-24 | 22-24 | 22-24 | 22-25 | 22-25 | 22-26 | 22-26 | 22-27 | 22-27 | 22-28 | 22-28 | 22-28 | 22-28 | 22-29 | 22-29 | 22-30 | 22-30 | 22-31 | 22-31 | 22-32 | 22-32 | 22-32 | 22-32 | 22-32 | 22-32 | 22-32 | 22-32
standard | ruleset_reference | [10 empty] | G3.1.3.8 | G3.1.3.8 | G3.1.3.8 | G3.1.3.8 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.9 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.9 | G3.1.3.9 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.7 | G3.1.3.7 | G3.1.3.7 | G3.1.3.7 | Table G3.5.3 | Table G3.5.3 | Table G3.5.3 | Table G3.5.3 | Table G3.5.3 | Table G3.5.3 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.10 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.11 | G3.1.3.7 | G3.1.3.7 | G3.1.3.7 | G3.1.3.7 | G3.1.3.7 | G3.1.3.7 | G3.1.3.7 | G3.1.3.7
standard | rule_description | [10 empty] | Baseline chilled water design supply temperature shall be modeled at 44F. | Baseline chilled water design supply temperature shall be modeled at 44F. | For applicable baseline system types 7, 8, 11, 12 and 13, the baseline chilled water design return temperature shall be modeled at 56F. | For applicable baseline system types 7, 8, 11, 12 and 13, the baseline chilled water design return temperature shall be modeled at 56F. | For Baseline chilled water loop that is not purchased cooling, chilled-water supply temperature shall be reset based on outdoor dry-bulb temperature if loop does not serve any Baseline System Type-11. | For Baseline chilled water loop that is not purchased cooling, chilled-water supply temperature shall be reset based on outdoor dry-bulb temperature if loop does not serve any Baseline System Type-11. | For baseline chilled water loop that is not purchased chilled water and does not serve any computer room HVAC systems, chilled-water supply temperature shall be reset using the following schedule: 44F at outdoor dry-bulb temperature of 80F and above, 54F at 60F and below, and ramped linearly between 44F and 54F at temperature between 80F and 60F. | For baseline chilled water loop that is not purchased chilled water and does not serve any computer room HVAC systems, chilled-water supply temperature shall be reset using the following schedule: 44F at outdoor dry-bulb temperature of 80F and above, 54F at 60F and below, and ramped linearly between 44F and 54F at temperature between 80F and 60F. | For baseline chilled water loop that is not purchased chilled water and does not serve any computer room HVAC systems, chilled-water supply temperature shall be reset using the following schedule: 44F at outdoor dry-bulb temperature of 80F and above, 54F at 60F and below, and ramped linearly between 44F and 54F at temperature between 80F and 60F. | For baseline chilled water loop that is not purchased chilled water and does not serve any computer room HVAC systems, chilled-water supply temperature shall be reset using the following schedule: 44F at outdoor dry-bulb temperature of 80F and above, 54F at 60F and below, and ramped linearly between 44F and 54F at temperature between 80F and 60F. | For baseline chilled water loop that is not purchased chilled water and does not serve any computer room HVAC systems, chilled-water supply temperature shall be reset using the following schedule: 44F at outdoor dry-bulb temperature of 80F and above, 54F at 60F and below, and ramped linearly between 44F and 54F at temperature between 80F and 60F. | For Baseline chilled water loop that is not purchased chilled water and serves computer room HVAC systems (Baseline System Type-11), chilled-water supply temperature shall be reset higher based on the HVAC system requiring the most cooling. | For Baseline chilled water loop that is not purchased chilled water and serves computer room HVAC systems (Baseline System Type-11), chilled-water supply temperature shall be reset higher based on the HVAC system requiring the most cooling. | For baseline chilled water loop that is not purchased chilled water and serves computer room HVAC systems (System Type-11), The maximum reset chilled-water supply temperature shall be 54F. | For baseline chilled water loop that is not purchased chilled water and serves computer room HVAC systems (System Type-11), The maximum reset chilled-water supply temperature shall be 54F. | Baseline chilled water system that does not use purchased chilled water shall be modeled as primary/secondary systems. | Baseline chilled water system that does not use purchased chilled water shall be modeled as primary/secondary systems. | Baseline chilled water system that does not use purchased chilled water shall be modeled as primary/secondary systems. | For baseline chilled water system with cooling capacity of 300 tons or more, the secondary pump shall be modeled with variable-speed drives. | For baseline chilled water system with cooling capacity of 300 tons or more, the secondary pump shall be modeled with variable-speed drives. | For baseline chilled water system with cooling capacity of 300 tons or more, the secondary pump shall be modeled with variable-speed drives. | For baseline chilled water system with cooling capacity of 300 tons or more, the secondary pump shall be modeled with variable-speed drives. | For Baseline chilled water system with cooling capacity of 300 tons or more, the secondary loop shall be modeled with a minimum flow of 25% of the design flow rate. | For Baseline chilled water system with cooling capacity of 300 tons or more, the secondary loop shall be modeled with a minimum flow of 25% of the design flow rate. | For Baseline chilled water system with cooling capacity less than 300ton, the secondary pump shall be modeled as riding the pump curve. | For Baseline chilled water system with cooling capacity less than 300ton, the secondary pump shall be modeled as riding the pump curve. | For Baseline chilled water system with cooling capacity less than 300ton, the secondary pump shall be modeled as riding the pump curve. | For Baseline chilled-water system that does not use purchased chilled water, variable-flow secondary pump shall be modeled as 13W/gpm at design conditions. | For Baseline chilled-water system that does not use purchased chilled water, variable-flow secondary pump shall be modeled as 13W/gpm at design conditions. | Baseline systems served by purchased chilled water shall not be modeled with chilled water reset | Baseline systems served by purchased chilled water shall not be modeled with chilled water reset | Baseline systems served by purchased chilled water shall be modeled with a chilled water distribution pump | Baseline systems served by purchased chilled water shall be modeled with a chilled water distribution pump | Baseline systems served by purchased chilled water loop shall be modeled with a distribution pump with a variable speed drive | Baseline systems served by purchased chilled water loop shall be modeled with a distribution pump with a variable speed drive | Baseline systems served by purchased chilled water loop shall have a minimum flow setpoint of 25% | Baseline systems served by purchased chilled water loop shall have a minimum flow setpoint of 25% | Baseline systems served by purchased chilled water loop shall be modeled with a distribution pump whose pump power is 16W/gpm | Baseline systems served by purchased chilled water loop shall be modeled with a distribution pump whose pump power is 16W/gpm | The heat rejection loop shall be modeled with a single cooling tower | The heat rejection loop shall be modeled with a single cooling tower | The heat rejection loop shall be modeled with a single cooling tower | The baseline heat rejection loop shall be an axial-fan open circuit cooling tower. | The baseline heat rejection loop shall be an axial-fan open circuit cooling tower. | The baseline heat-rejection device shall have a design temperature rise of 10°F. | The baseline heat-rejection device shall have a design temperature rise of 10°F. | Design Wet Bulb is 0.4% evaporation design wet-bulb temperature, ranging from 12.8C<=WB<=32.2C? (55F->90F) | Design Wet Bulb is 0.4% evaporation design wet-bulb temperature, ranging from 12.8C<=WB<=32.2C? (55F->90F) | Design Wet Bulb is 0.4% evaporation design wet-bulb temperature, ranging from 12.8C<=WB<=32.2C? (55F->90F) | Heat Rejection Device Approach calaculated correctly (T/F), Approach = 25.72-(0.24*WB) | Heat Rejection Device Approach calaculated correctly (T/F), Approach = 25.72-(0.24*WB) | The baseline condenser-water design supply temperature shall be calculated using the cooling tower approach to the 0.4% evaporation design wet-bulb temperature, valid for wet-bulbs from 55°F to 90°F. | The baseline condenser-water design supply temperature shall be calculated using the cooling tower approach to the 0.4% evaporation design wet-bulb temperature, valid for wet-bulbs from 55°F to 90°F. | The baseline heat rejection device shall have an efficiency of 38.2 gpm/hp | The baseline heat rejection device shall have an efficiency of 38.2 gpm/hp | The baseline heat rejection device shall be modeled with variable speed fan control | The baseline heat rejection device shall be modeled with variable speed fan control | The baaseline cooling tower shall be controlled to maintain a leaving water temperature, where weather permits, as specified in Table G3.1.3.11 | The baaseline cooling tower shall be controlled to maintain a leaving water temperature, where weather permits, as specified in Table G3.1.3.11 | The baseline condenser loop minimum condenser leaving water temperature shall be modeled as specified in Table G3.1.3.11. | The baseline condenser loop minimum condenser leaving water temperature shall be modeled as specified in Table G3.1.3.11. | The baseline condenser loop minimum condenser leaving water temperature shall be modeled as specified in Table G3.1.3.11. | The baseline condenser loop minimum condenser leaving water temperature shall be modeled as specified in Table G3.1.3.11. | The baseline condenser loop minimum condenser leaving water temperature shall be modeled as specified in Table G3.1.3.11. | The baseline building design’s chiller plant shall be modeled with chillers having the type as indicated in Table G3.1.3.7 as a function of building peak cooling load. | The baseline building design’s chiller plant shall be modeled with chillers having the type as indicated in Table G3.1.3.7 as a function of building peak cooling load. | The baseline building design’s chiller plant shall be modeled with chillers having the type as indicated in Table G3.1.3.7 as a function of building peak cooling load. | The baseline building design’s chiller plant shall be modeled with chillers having the type as indicated in Table G3.1.3.7 as a function of building peak cooling load. | The baseline chiller efficiencies shall be modeled at the minimum efficiency levels for full load, in accordance with Tables G3.5.3. | The baseline chiller efficiencies shall be modeled at the minimum efficiency levels for full load, in accordance with Tables G3.5.3. | The baseline chiller efficiencies shall be modeled at the minimum efficiency levels for full load, in accordance with Tables G3.5.3. | The baseline chiller efficiencies shall be modeled at the minimum efficiency levels for full load, in accordance with Tables G3.5.3. | The baseline chiller efficiencies shall be modeled at the minimum efficiency levels for full load, in accordance with Tables G3.5.3. | The baseline chiller efficiencies shall be modeled at the minimum efficiency levels for full load, in accordance with Tables G3.5.3. | Each baseline chiller shall be modeled with separate chilled water pump interlocked to operate with the associated chiller. | Each baseline chiller shall be modeled with separate chilled water pump interlocked to operate with the associated chiller. | Each baseline chiller shall be modeled with separate chilled water pump interlocked to operate with the associated chiller. | For baseline chilled-water systems served by chiller(s), the primary pump shall be modeled as constant volume. | For baseline chilled-water systems served by chiller(s), the primary pump shall be modeled as constant volume. | For chilled-water systems served by chiller(s) and does not serve baseline System-11, the baseline building constant-volume primary pump power shall be modeled as 9 W/gpm. | For chilled-water systems served by chiller(s) and does not serve baseline System-11, the baseline building constant-volume primary pump power shall be modeled as 9 W/gpm. | For chilled-water systems served by chiller(s) and serves baseline System-11, the baseline building constant-volume primary pump power shall be modeled as 12 W/gpm. | For chilled-water systems served by chiller(s) and serves baseline System-11, the baseline building constant-volume primary pump power shall be modeled as 12 W/gpm. | Each baseline chiller shall be modeled with separate condenser-water pump interlocked to operate with the associated chiller. | Each baseline chiller shall be modeled with separate condenser-water pump interlocked to operate with the associated chiller. | Each baseline chiller shall be modeled with separate condenser-water pump interlocked to operate with the associated chiller. | Each baseline chiller shall be modeled with separate condenser-water pump interlocked to operate with the associated chiller. | The baseline building design condenser-water pump shall be modeled as constant volume. | The baseline building design condenser-water pump shall be modeled as constant volume. | For chilled-water systems served by chiller(s) and does not serve baseline System-11, condenser-water pump power shall be 19 W/gpm. | For chilled-water systems served by chiller(s) and does not serve baseline System-11, condenser-water pump power shall be 19 W/gpm. | For chilled-water systems served by chiller(s) and serves baseline System-11, condenser-water pump power shall be 22 W/gpm. | For chilled-water systems served by chiller(s) and serves baseline System-11, condenser-water pump power shall be 22 W/gpm. | The baseline building design’s chiller plant shall be modeled with chillers having the number as indicated in Table G3.1.3.7 as a function of building peak cooling load | The baseline building design’s chiller plant shall be modeled with chillers having the number as indicated in Table G3.1.3.7 as a function of building peak cooling load | The baseline building design’s chiller plant shall be modeled with chillers having the number as indicated in Table G3.1.3.7 as a function of building peak cooling load | The baseline building design’s chiller plant shall be modeled with chillers having the number as indicated in Table G3.1.3.7 as a function of building peak cooling load | The baseline building design’s chiller plant shall be modeled with chillers having the number as indicated in Table G3.1.3.7 as a function of building peak cooling load | The baseline building design’s chiller plant shall be modeled with chillers having the number as indicated in Table G3.1.3.7 as a function of building peak cooling load | The baseline building design’s chiller plant shall be modeled with chillers having the number as indicated in Table G3.1.3.7 as a function of building peak cooling load | The baseline building design’s chiller plant shall be modeled with chillers having the number as indicated in Table G3.1.3.7 as a function of building peak cooling load
standard | applicable_rmr | [10 empty] | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR
standard | rule_assertion | bar: a to h
standard | comparison_value | [10 empty] | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value
standard | rule_dependency | [10 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
standard | mandatory_rule | [10 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes | Yes | Delete | Delete | Delete | No | No | Yes | Yes | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
standard | schema_version | [10 empty] | a: 0.0.5; b: 0.0.5; a: 0.0.5; b: 0.0.5; a: 0.0.5; b: 0.0.5; a: 0.0.5; b: 0.0.5; c: 0.0.5; d: 0.0.5; e: 0.0.5; a: 0.0.5; b: 0.0.5; a: 0.0.5; b: 0.0.5; a: 0.0.5; b: 0.0.5; c: 0.0.5; a: 0.0.5; b: 0.0.5; c: 0.0.5; d: 0.0.5; a: 0.0.5; b: 0.0.5; a: 0.0.5; b: 0.0.5; c: 0.0.5
template_lookup | [11 empty] | rule-22-1-a | rule-22-1-b | rule-22-2-a | rule-22-2-b | rule-22-3-a | rule-22-3-b | rule-22-4-a | rule-22-4-b | rule-22-4-c | rule-22-4-d | rule-22-4-e | rule-22-5-a | rule-22-5-b | rule-22-6-a | rule-22-6-b | rule-22-7-a | rule-22-7-b | rule-22-7-c | rule-22-8-a | rule-22-8-b | rule-22-8-c | rule-22-8-d | rule-22-9-a | rule-22-9-b | rule-22-10-a | rule-22-10-b | rule-22-10-c | rule-22-11-a | rule-22-11-b | rule-18-1-a | rule-18-1-b | rule-18-2-a | rule-18-2-b | rule-18-3-a | rule-18-3-b | rule-18-4-a | rule-18-4-b | rule-18-5-a | rule-18-5-b | rule-22-12-a | rule-22-12-b | rule-22-12-c | rule-22-13-a | rule-22-13-b | rule-22-14-a | rule-22-14-b | rule-22-15-a | rule-22-15-b | rule-22-15-c | rule-22-16-a | rule-22-16-b | rule-22-17-a | rule-22-17-b | rule-22-18-a | rule-22-18-b | rule-22-19-a | rule-22-19-b | rule-22-20-a | rule-22-20-b | rule-22-21-a | rule-22-21-b | rule-22-21-c | rule-22-21-d | rule-22-21-e | rule-22-22-a | rule-22-22-b | rule-22-22-c | rule-22-22-d | rule-22-23-a | rule-22-23-b | rule-22-23-c | rule-22-23-d | rule-22-23-e | rule-22-23-f | rule-22-24-a | rule-22-24-b | rule-22-24-c | rule-22-25-a | rule-22-25-b | rule-22-26-a | rule-22-26-b | rule-22-27-a | rule-22-27-b | rule-22-28-a | rule-22-28-b | rule-22-28-c | rule-22-28-d | rule-22-29-a | rule-22-29-b | rule-22-30-a | rule-22-30-b | rule-22-31-a | rule-22-31-b | rule-22-32-a | rule-22-32-b | rule-22-32-c | rule-22-32-d | rule-22-32-e | rule-22-32-f | rule-22-32-g | rule-22-32-h
rmr_template | user
rmr_template | proposed
rmr_template | baseline | [10 empty] | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true
rmr_template | json_template | id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | TODO | TODO | TODO | TODO | TODO | TODO | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
rmr_template | json_template | weather | climate_zone |  |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone |  |  | a: CZ5C; b: CZ3C; c: CZ4A; d: CZ1A; e: CZ5C
rmr_template | json_template | buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | a: Building 1; b: Building 1; a: Building 1; b: Building 1; a: Building 1; b: Building 1
rmr_template | json_template | buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | a: Required Building Schedule 1; b: Required Building Schedule 1; a: Required Building Schedule 1; b: Required Building Schedule 1; a: Required Building Schedule 1; b: Required Building Schedule 1
rmr_template | json_template | JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | a: Building Segment 1; b: Building Segment 1; a: Building Segment 1; b: Building Segment 1; a: Building Segment 1; b: Building Segment 1
rmr_template | json_template | JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | a: Thermal Zone 1; b: Thermal Zone 1; a: Thermal Zone 1; b: Thermal Zone 1; a: Thermal Zone 1; b: Thermal Zone 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | a: Required Cooling Schedule 1; b: Required Cooling Schedule 1; a: Required Cooling Schedule 1; b: Required Cooling Schedule 1; a: Required Cooling Schedule 1; b: Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | a: Required Heating Schedule 1; b: Required Heating Schedule 1; a: Required Heating Schedule 1; b: Required Heating Schedule 1; a: Required Heating Schedule 1; b: Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | a: VAV Air Terminal 1; b: VAV Air Terminal 1; a: VAV Air Terminal 1; b: VAV Air Terminal 1; a: VAV Air Terminal 1; b: VAV Air Terminal 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | a: true; b: true; a: true; b: true; a: true; b: true
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | reheat_source |  | Air Terminal | Terminal 1 | Zone 1 | reheat_source |  |  | a: HOT_WATER; b: HOT_WATER; a: HOT_WATER; b: HOT_WATER; a: HOT_WATER; b: HOT_WATER
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | a: VARIABLE_AIR_VOLUME; b: VARIABLE_AIR_VOLUME; a: VARIABLE_AIR_VOLUME; b: VARIABLE_AIR_VOLUME; a: VARIABLE_AIR_VOLUME; b: VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilation_air_conditioning_systems |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilation_air_conditioning_systems |  |  | a: VAV System 1; b: VAV System 1; a: VAV System 1; b: VAV System 1; a: VAV System 1; b: VAV System 1
rmr_template | json_template | JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | reheat_source |  | Air Terminal | Terminal 2 | Zone 2 | reheat_source
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilation_air_conditioning_systems |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilation_air_conditioning_systems
rmr_template | json_template | JSON_PATH:heating_ventilation_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | a: System Type 11; b: System Type 11; a: System Type 11; b: System Type 11; a: System Type 11; b: System Type 11
rmr_template | json_template | JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | a: CHW Coil 1; b: CHW Coil 1; a: CHW Coil 1; b: CHW Coil 1; a: CHW Coil 1; b: CHW Coil 1
rmr_template | json_template | JSON_PATH:cooling_system | cooling_system_type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | a: FLUID_LOOP; b: FLUID_LOOP; a: FLUID_LOOP; b: FLUID_LOOP; a: FLUID_LOOP; b: FLUID_LOOP
rmr_template | json_template | JSON_PATH:cooling_system | dehumidification_type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | dehumidification_type
rmr_template | json_template | JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  | a: HHW Coil 1; b: HHW Coil 1; a: HHW Coil 1; b: HHW Coil 1; a: HHW Coil 1; b: HHW Coil 1
rmr_template | json_template | JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  | a: FLUID_LOOP; b: FLUID_LOOP; a: FLUID_LOOP; b: FLUID_LOOP; a: FLUID_LOOP; b: FLUID_LOOP
rmr_template | json_template | JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | a: Boiler Loop 1; b: Boiler Loop 1; a: Boiler Loop 1; b: Boiler Loop 1; a: Boiler Loop 1; b: Boiler Loop 1
rmr_template | json_template | JSON_PATH:fan_systems[0] | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | a: VAV Fan System 1; b: VAV Fan System 1; a: VAV Fan System 1; b: VAV Fan System 1; a: VAV Fan System 1; b: VAV Fan System 1
rmr_template | json_template | JSON_PATH:fan_systems[0] | is_variable_air_volume |  |  | Fan System | Fan System 1 | HVAC 1 | is_variable_air_volume |  |  | a: true; b: true; a: true; b: true; a: true; b: true
rmr_template | json_template | JSON_PATH:fan_systems[0] | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | a: VARIABLE_SPEED_DRIVE; b: VARIABLE_SPEED_DRIVE; a: VARIABLE_SPEED_DRIVE; b: VARIABLE_SPEED_DRIVE; a: VARIABLE_SPEED_DRIVE; b: VARIABLE_SPEED_DRIVE
rmr_template | json_template | JSON_PATH:fan_systems[0] | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | a: Supply Fan 1; b: Supply Fan 1; a: Supply Fan 1; b: Supply Fan 1; a: Supply Fan 1; b: Supply Fan 1
rmr_template | json_template | JSON_PATH:fan_systems[0] | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | a: Return Fan 1; b: Return Fan 1; a: Return Fan 1; b: Return Fan 1; a: Return Fan 1; b: Return Fan 1
rmr_template | json_template | boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | a: Boiler 1; b: Boiler 1; a: Boiler 1; b: Boiler 1; a: Boiler 1; b: Boiler 1
rmr_template | json_template | boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | a: NATURAL_GAS; b: NATURAL_GAS; a: NATURAL_GAS; b: NATURAL_GAS; a: NATURAL_GAS; b: NATURAL_GAS
rmr_template | json_template | boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | a: Boiler Loop 1; b: Boiler Loop 1; a: Boiler Loop 1; b: Boiler Loop 1; a: Boiler Loop 1; b: Boiler Loop 1
rmr_template | json_template | chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id |  |  | a: Chiller 1; b: Chiller 1; a: Chiller 1; b: Chiller 1; a: Chilled Water 1; b: Chilled Water 1; c: Chilled Water 1; d: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; c: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; c: Chilled Water 1; d: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; c: Chilled Water 1; d: Chilled Water 1; e: Chilled Water 1; f: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; c: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; a: Chiller 1; b: Chiller 1; a: Chiller 1; b: Chiller 1; c: Chiller 1; d: Chiller 1; a: Chiller 1; b: Chiller 1; a: Chiller 1; b: Chiller 1; a: Chiller 1; b: Chiller 1; a: Chiller 1; b: Chiller 1; c: Chiller 1; d: Chiller 1; e: Chiller 1; f: Chiller 1; g: Chiller 1; h: Chiller 1
rmr_template | json_template | chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop |  |  | a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; c: Chilled Water Loop 1; d: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; c: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; c: Chilled Water Loop 1; d: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; c: Chilled Water Loop 1; d: Chilled Water Loop 1; e: Chilled Water Loop 1; f: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; c: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; c: Chiller Loop 1; d: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; c: Chiller Loop 1; d: Chiller Loop 1; e: Chiller Loop 1; f: Chiller Loop 1; g: Chiller Loop 1; h: Chiller Loop 1
rmr_template | json_template | chillers[0] | design_capacity |  |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton | a: 400; b: 300; c: 400; d: 250; a: 250; b: 250; c: 250; a: 599; b: 600; c: 550; d: 700; a: 149; b: 299; c: 300; d: 300; e: 299; f: 149; a: 300; b: 300; c: 300; d: 800; e: 800; f: 600; g: 500; h: 900
rmr_template | json_template | chillers[0] | energy_source_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type |  |  | a: ELECTRICITY; b: ELECTRICITY; a: ELECTRICITY; b: ELECTRICITY; a: ELECTRICITY; b: ELECTRICITY
rmr_template | json_template | chillers[0] | full_load_efficiency |  |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton | a: 0.79; b: 0.718; c: 0.526; d: 0.718; e: 0.576; f: 0.676
rmr_template | json_template | chillers[0] | compressor_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type |  |  | a: SCREW; b: CENTRIFUGAL; c: CENTRIFUGAL; d: SCREW; a: SCREW; b: SCREW; c: CENTRIFUGAL; d: CENTRIFUGAL; e: SCREW; f: SCREW
rmr_template | json_template | chillers[1] | id |  |  | Chiller | Chiller 2 | ASHRAE229 1 | id |  |  | b: Chiller 2; c: Chiller 2; d: Chiller 2; e: Chiller 2; g: Chiller 2
rmr_template | json_template | chillers[1] | cooling_loop |  |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop |  |  | b: Chiller Loop 1; c: Chiller Loop 1; d: Chiller Loop 1; e: Chiller Loop 1; g: Chiller Loop 1
rmr_template | json_template | chillers[1] | design_capacity |  |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton | b: 300; c: 300; d: 800; e: 800; g: 500
rmr_template | json_template | chillers[2] | id |  |  | Chiller | Chiller 3 | ASHRAE229 1 | id |  |  | d: Chiller 3; e: Chiller 3; g: Chiller 3
rmr_template | json_template | chillers[2] | cooling_loop |  |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop |  |  | d: Chiller Loop 1; e: Chiller Loop 1; g: Chiller Loop 1
rmr_template | json_template | chillers[2] | design_capacity |  |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton | d: 800; e: 800; g: 500
rmr_template | json_template | chillers[3] | id |  |  | Chiller | Chiller 4 | ASHRAE229 1 | id |  |  | e: Chiller 4; g: Chiller 4
rmr_template | json_template | chillers[3] | cooling_loop |  |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop |  |  | e: Chiller Loop 1; g: Chiller Loop 1
rmr_template | json_template | chillers[3] | design_capacity |  |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton | e: 800; g: 500
rmr_template | json_template | heat_rejections[0] | id |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id |  |  | a: Cooling Tower 1; c: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; c: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; c: Cooling Tower 1; d: Cooling Tower 1; e: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; c: Cooling Tower 1; d: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; c: Cooling Tower 1; d: Cooling Tower 1; e: Cooling Tower 1; f: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1; a: Cooling Tower 1; b: Cooling Tower 1
rmr_template | json_template | heat_rejections[0] | loop |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop |  |  | a: Condensing Water Loop 1; c: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; c: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; c: Condensing Water Loop 1; d: Condensing Water Loop 1; e: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; c: Condensing Water Loop 1; d: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; c: Condensing Water Loop 1; d: Condensing Water Loop 1; e: Condensing Water Loop 1; f: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1
rmr_template | json_template | heat_rejections[0] | type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type |  |  | a: OPEN_CIRCUIT_COOLING_TOWER; c: OPEN_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: DRY_COOLER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; c: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; c: CLOSED_CIRCUIT_COOLING_TOWER; d: CLOSED_CIRCUIT_COOLING_TOWER; e: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; c: CLOSED_CIRCUIT_COOLING_TOWER; d: CLOSED_CIRCUIT_COOLING_TOWER; a: CLOSED_CIRCUIT_COOLING_TOWER; b: CLOSED_CIRCUIT_COOLING_TOWER; c: CLOSED_CIRCUIT_COOLING_TOWER; d: CLOSED_CIRCUIT_COOLING_TOWER; e: CLOSED_CIRCUIT_COOLING_TOWER; f: CLOSED_CIRCUIT_COOLING_TOWER
rmr_template | json_template | heat_rejections[0] | design_supply_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_supply_temperature | temperature | F | a: 85; b: 83
rmr_template | json_template | heat_rejections[0] | design_water_flowrate |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min | a: 51; b: 40
rmr_template | json_template | heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F | a: 75; b: 52; c: 92; a: 73.4; b: 73.4; a: 73.4; b: 73.4
rmr_template | json_template | heat_rejections[0] | fan_power |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_power | electric_power | W | a: 1000; b: 1000
rmr_template | json_template | heat_rejections[0] | fan_speed_control |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control |  |  | a: VARIABLE_SPEED; b: TWO_SPEED
rmr_template | json_template | heat_rejections[0] | range |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature | F | a: 42; b: 40; a: 42; b: 40
rmr_template | json_template | heat_rejections[0] | reset_type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type |  |  | a: LOAD_RESET; b: OTHER
rmr_template | json_template | heat_rejections[0] | minimum_reset_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | minimum_reset_temperature | temperature | F | a: 65; b: 70; c: 75; d: 80; e: 80
rmr_template | json_template | heat_rejections[1] | id |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id |  |  | c: Cooling Tower 2
rmr_template | json_template | heat_rejections[1] | loop |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | loop |  |  | c: Condensing Water Loop 1
rmr_template | json_template | heat_rejections[1] | type |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | type |  |  | c: OPEN_CIRCUIT_COOLING_TOWER
rmr_template | json_template | external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id |  |  | a: Chilled Water 1; b: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; c: Chilled Water 1; d: Chilled Water 1; e: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1; c: Chilled Water 1; a: Chilled Water 1; b: Chilled Water 1
rmr_template | json_template | external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop |  |  | a: Chilled Water Loop 1; b: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; c: Chilled Water Loop 1; d: Chilled Water Loop 1; e: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1; c: Chilled Water Loop 1; a: Chilled Water Loop 1; b: Chilled Water Loop 1
rmr_template | json_template | external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type |  |  | a: CHILLED_WATER; b: CHILLED_WATER; a: CHILLED_WATER; b: CHILLED_WATER; a: CHILLED_WATER; b: CHILLED_WATER; a: CHILLED_WATER; b: CHILLED_WATER; c: CHILLED_WATER; d: CHILLED_WATER; e: CHILLED_WATER; a: CHILLED_WATER; b: CHILLED_WATER; c: CHILLED_WATER; a: CHILLED_WATER; b: CHILLED_WATER
rmr_template | json_template | pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id |  |  | a: Boiler Pump 1; b: Boiler Pump 1; a: Boiler Pump 1; b: Boiler Pump 1; a: Primary Pump 1; b: Primary Pump 1; c: Primary Pump 1; a: Primary Pump 1; b: Primary Pump 1; c: Primary Pump 1; d: Primary Pump 1; a: Primary Pump 1; b: Primary Pump 1; a: Primary Pump 1; b: Primary Pump 1; c: Primary Pump 1; a: Primary Pump 1; b: Primary Pump 1; a: Primary Pump 1; b: Primary Pump 1; a: Primary Pump 1; c: Secondary Pump 1; a: Primary Pump 1; b: Primary Pump 1; a: Primary Pump 1; b: Primary Pump 1; a: Boiler Pump 1; b: Boiler Pump 1; a: Condensing Water Pump 1; b: Chiller Pump 1; a: Condensing Water Pump 1; b: Condensing Water Pump 1; a: Condensing Water Pump 1; b: Condensing Water Pump 1; a: Chiller Pump 1; b: Chiller Pump 1
rmr_template | json_template | pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping |  |  | a: Boiler Loop 1; b: Boiler Loop 1; a: Boiler Loop 1; b: Boiler Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; c: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; c: Chiller Loop 1; d: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; c: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; c: Secondary Water Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Boiler Loop 1; b: Boiler Loop 1; a: Condensing Water Loop 1; b: Chiller Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Chiller Loop 1; b: Chiller Loop 1
rmr_template | json_template | pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control |  |  | a: FIXED_SPEED; b: FIXED_SPEED; a: FIXED_SPEED; b: FIXED_SPEED; a: FIXED_SPEED; b: FIXED_SPEED; c: FIXED_SPEED; d: FIXED_SPEED; a: FIXED_SPEED; b: FIXED_SPEED; c: FIXED_SPEED; a: FIXED_SPEED; b: FIXED_SPEED; a: FIXED_SPEED; b: FIXED_SPEED; a: FIXED_SPEED; b: VARIABLE_SPEED; a: FIXED_SPEED; b: FIXED_SPEED; a: FIXED_SPEED; b: VARIABLE_SPEED
rmr_template | json_template | pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W | a: 900; b: 1000; a: 1900; b: 2200; a: 2200; b: 2000
rmr_template | json_template | pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min | a: 100; b: 100; a: 100; b: 100; a: 100; b: 100
rmr_template | json_template | pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
rmr_template | json_template | pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
rmr_template | json_template | pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
rmr_template | json_template | pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id |  |  | a: Chiller Pump 1; b: Chiller Pump 1; a: Chiller Pump 1; b: Chiller Pump 1; a: Secondary Pump 1; b: Primary Pump 2; a: Secondary Pump 1; b: Secondary Pump 1; c: Secondary Pump 1; d: Secondary Pump 1; a: Secondary Pump 1; b: Secondary Pump 1; a: Secondary Pump 1; b: Secondary Pump 1; c: Secondary Pump 1; a: Secondary Pump 1; b: Secondary Pump 1; a: Secondary Pump 1; b: Secondary Pump 1; a: Chiller Pump 1; b: Chiller Pump 1
rmr_template | json_template | pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping |  |  | a: Chiller Loop 1; b: Chiller Loop 1; a: Chiller Loop 1; b: Chiller Loop 1; a: Secondary Water Loop 1; b: Chiller Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; c: Secondary Water Loop 1; d: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; c: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; a: Chiller Loop 1; b: Chiller Loop 1
rmr_template | json_template | pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control |  |  | a: FIXED_SPEED; b: FIXED_SPEED; a: FIXED_SPEED; b: FIXED_SPEED; a: VARIABLE_SPEED; b: VARIABLE_SPEED; d: VARIABLE_SPEED; a: VARIABLE_SPEED; b: VARIABLE_SPEED; a: VARIABLE_SPEED; b: VARIABLE_SPEED; c: FIXED_SPEED; a: VARIABLE_SPEED; b: VARIABLE_SPEED; a: VARIABLE_SPEED; b: VARIABLE_SPEED; a: FIXED_SPEED; b: FIXED_SPEED
rmr_template | json_template | pumps[1] | design_electric_power |  |  | Pump | Pump 2 | ASHRAE229 1 | design_electric_power | electric_power | W | a: 1300; b: 1500; a: 1200; b: 1400
rmr_template | json_template | pumps[1] | design_flow |  |  | Pump | Pump 2 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min | a: 100; b: 100; a: 100; b: 100
rmr_template | json_template | pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id
rmr_template | json_template | pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping
rmr_template | json_template | fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id |  |  | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | [6 empty] | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Condensing Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1
rmr_template | json_template | fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type |  |  | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | [6 empty] | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | CONDENSER | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING |  |  |  |  | HEATING | HEATING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING
rmr_template | json_template | fluid_loops[0] | cooling_or_condensing_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id |  |  | a: Cool DAC 1; b: Cool DAC 1; a: Cool DAC 1; b: Cool DAC 1; a: Cool DAC 1; b: Cool DAC 1; a: Cool DAC 1; b: Cool DAC 1; c: Cool DAC 1; d: Cool DAC 1; e: Cool DAC 1; a: Cool DAC 1; b: Cool DAC 1; a: Cool DAC 1; b: Cool DAC 1; a: Cool DAC 1; b: Cool DAC 1
rmr_template | json_template | fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F | a: 44; b: 41
rmr_template | json_template | fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F | a: 56; b: 50
rmr_template | json_template | fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type |  |  | a: OUTSIDE_AIR_RESET; b: NO_RESET; a: OUTSIDE_AIR_RESET; b: OUTSIDE_AIR_RESET; c: OUTSIDE_AIR_RESET; d: OUTSIDE_AIR_RESET; e: OUTSIDE_AIR_RESET; a: LOAD_RESET; b: NO_RESET; a: NO_RESET; b: LOAD_RESET
rmr_template | json_template | fluid_loops[0] | cooling_or_condensing_design_and_control | outdoor_high_for_loop_supply_temperature_reset |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_high_for_loop_supply_temperature_reset | temperature | F | a: 54; b: 50
rmr_template | json_template | fluid_loops[0] | cooling_or_condensing_design_and_control | outdoor_low_for_loop_supply_temperature_reset |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_low_for_loop_supply_temperature_reset | temperature | F
rmr_template | json_template | fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
rmr_template | json_template | fluid_loops[0] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 1 | id |  |  | a: Secondary Water Loop 1; b: Secondary Water Loop 1; c: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; c: Secondary Water Loop 1; d: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; c: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; a: Secondary Water Loop 1; b: Secondary Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; c: Condensing Water Loop 1; d: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; c: Condensing Water Loop 1; d: Condensing Water Loop 1; e: Condensing Water Loop 1; f: Condensing Water Loop 1; c: Secondary Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1; a: Condensing Water Loop 1; b: Condensing Water Loop 1
rmr_template | json_template | fluid_loops[0] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 1 | type |  |  | a: COOLING; b: COOLING; c: COOLING; a: COOLING; b: COOLING; c: COOLING; d: COOLING; a: COOLING; b: COOLING; a: COOLING; b: COOLING; c: COOLING; a: COOLING; b: COOLING; a: COOLING; b: COOLING; a: CONDENSER; b: CONDENSER; c: CONDENSER; d: CONDENSER; a: CONDENSER; b: CONDENSER; c: CONDENSER; d: CONDENSER; e: CONDENSER; f: CONDENSER; c: COOLING; a: CONDENSER; b: CONDENSER; a: CONDENSER; b: CONDENSER; a: CONDENSER; b: CONDENSER
rmr_template | json_template | fluid_loops[0] | child_loops[0] | cooling_or_condensing_design_and_control | id | [6 empty] | a: Cool DAC 1; b: Cool DAC 1
rmr_template | json_template | fluid_loops[0] | child_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction | FluidLoopDesignAndControl | DAC 2 | SecondaryLoop 1 | minimum_flow_fraction |  |  | a: 0.25; b: 0.4
rmr_template | json_template | fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id |  |  | a: HEATING; b: HEATING; a: HEATING; b: HEATING; a: Chiller Loop 1; b: Chiller Loop 1
|  | fluid_loops[1] | type

## HVAC_TCDs (hidden)
key1 | key2 | key3 | key4 | key5 | data_group | object_id | parent_id | data_element | unit_type | units | System_1_PTAC | System_3_PSZ_AC | System_7_VAV_HW_Reheat
Section | [10 empty] | 99 | 99 | 99
Rule | [10 empty] | 1 | 2 | 3
Test | [10 empty] | a | a | a
Notes
test_description | [10 empty] | dummy | dummy | dummy
expected_rule_outcome | [10 empty] | pass | pass | pass
template_lookup | [10 empty] | System_1_PTAC | System_3_PSZ_AC | System_7_VAV_HW_Reheat
rmr_template | user | [9 empty] | true | true | true
rmr_template | proposed
rmr_template | baseline
rmr_template | json_template | id |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | #N/A | ASHRAE229 1
rmr_template | json_template | weather | climate_zone |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone |  |  |  | #N/A
rmr_template | json_template | calendar | day_of_week_for_january_1 |  | ASHRAE229 | ASHRAE229 1 | calendar | day_of_week_for_january_1 |  |  |  | #N/A
rmr_template | json_template | ruleset_model_descriptions[0] | id |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | #N/A | RMD 1
rmr_template | json_template | JSON_PATH:buildings[0] | id |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | #N/A | Building 1
rmr_template | json_template | JSON_PATH:buildings[0] | building_open_schedule |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | #N/A | Required Building Schedule 1
rmr_template | json_template | JSON_PATH: building_segments[0] | id |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | #N/A | Building Segment 1
rmr_template | json_template | JSON_PATH:zones[0] | id |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | #N/A | Thermal Zone 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | #N/A | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | #N/A | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | id | Space | Space 1 | Zone 1 | id |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule | Space | Space 1 | Zone 1 | occupant_multiplier_schedule |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | floor_area | Space | Space 1 | Zone 1 | floor_area | area | ft2 |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | id | Air Terminal | Terminal 1 | Zone 1 | id |  |  | PTAC Terminal 1 | #N/A | VAV Air Terminal 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | false | #N/A | true
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | type | Air Terminal | Terminal 1 | Zone 1 | type |  |  | CONSTANT_AIR_VOLUME | #N/A | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_systems |  |  | PTAC 1 | #N/A | System 7
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_source | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  |  | #N/A | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_from_loop | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  |  | #N/A | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_source | Air Terminal | Terminal 1 | Zone 1 | cooling_source |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop | Air Terminal | Terminal 1 | Zone 1 | cooling_from_loop |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan | Air Terminal | Terminal 1 | Zone 1 | fan |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan_configuration | Air Terminal | Terminal 1 | Zone 1 | fan_configuration |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | id |  | Zone | Zone 2 | Building Segment 1 | id |  |  |  | #N/A | Thermal Zone 2
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  |  | #N/A | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  |  | #N/A | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | id | Space | Space 2 | Zone 2 | id |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule | Space | Space 2 | Zone 2 | occupant_multiplier_schedule |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | floor_area | Space | Space 2 | Zone 2 | floor_area | area | ft2 |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | id | Air Terminal | Terminal 2 | Zone 2 | id |  |  |  | #N/A | VAV Air Terminal 2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  |  | #N/A | TRUE
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | type | Air Terminal | Terminal 2 | Zone 2 | type |  |  |  | #N/A | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_systems |  |  |  | #N/A | System 7
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  |  | #N/A | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_from_loop | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop |  |  |  | #N/A | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | cooling_source | Air Terminal | Terminal 2 | Zone 2 | cooling_source |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | cooling_from_loop | Air Terminal | Terminal 2 | Zone 2 | cooling_from_loop |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan | Air Terminal | Terminal 2 | Zone 2 | fan |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan_configuration | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | PTAC 1 | #N/A | System 7
rmr_template | json_template | JSON_PATH:cooling_system | id |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | DX Coil 1 | #N/A | CHW Coil 1
rmr_template | json_template | JSON_PATH:cooling_system | type |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | DIRECT_EXPANSION | #N/A | FLUID_LOOP
rmr_template | json_template | JSON_PATH:cooling_system | chilled_water_loop |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop |  |  |  | #N/A | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:heating_system | id |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  | HHW Coil 1 | #N/A
rmr_template | json_template | JSON_PATH:heating_system | type |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  | FLUID_LOOP | #N/A
rmr_template | json_template | JSON_PATH:heating_system | energy_source_type |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:heating_system | hot_water_loop |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | Boiler Loop 1 | #N/A
rmr_template | json_template | JSON_PATH:preheat_system | id |  | PreheatSystem | Heating System 1 | HVAC 1 | id |  |  |  | #N/A | Preheat Coil 1
rmr_template | json_template | JSON_PATH:preheat_system | type |  | PreheatSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  |  | #N/A | FLUID_LOOP
rmr_template | json_template | JSON_PATH:preheat_system | hot_water_loop |  | PreheatSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  |  | #N/A | Boiler Loop 1
rmr_template | json_template | JSON_PATH:fan_system | id |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | CAV Fan System 1 | #N/A | VAV Fan System 1
|  | JSON_PATH:fan_system | fan_control |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | CONSTANT | #N/A | VARIABLE_SPEED_DRIVE
|  | JSON_PATH:fan_system | supply_fans[0] | id | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | #N/A | Supply Fan 1
|  | JSON_PATH:fan_system | return_fans[0] | id | Fan | Return Fan 1 | HVAC 1 | id |  |  |  | #N/A | Return Fan 1
|  |  | id |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1 | #N/A | Boiler 1
rmr_transformations | user | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | proposed | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | baseline | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2

## Lighting_TCDs (hidden)
key1 | key2 | key3 | key4 | key5 | data_group | object_id | parent_id | data_element | unit_type | units | Lighting Example
Section | [10 empty] | 99
Rule | [10 empty] | 1
Test | [10 empty] | a
Notes
test_description | [10 empty] | dummy
expected_rule_outcome | [10 empty] | pass
template_lookup | [10 empty] | Lighting Example
rmr_template | user | [9 empty] | true
rmr_template | proposed
rmr_template | baseline
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[9 empty] | #REF! | #REF!
rmr_transformations | user | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | proposed | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | baseline | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2

## Envelope_TCDs (hidden)
key1 | key2 | key3 | key4 | key5 | data_group | object_id | parent_id | data_element | unit_type | units | Envelope_Example
Section | [10 empty] | 99
Rule | [10 empty] | 1
Test | [10 empty] | a
Notes
test_description | [10 empty] | dummy
expected_rule_outcome | [10 empty] | pass
template_lookup | [10 empty] | Envelope_Example
rmr_template | user | [9 empty] | true
rmr_template | proposed
rmr_template | baseline
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_transformations | user | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | proposed | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | baseline | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2

## TCD_old (hidden)
appendix_g_section_id | rule_id | test_id | case_number | rule_description | test_outcome | user_rmr_xpath | test_type | target_rmr | test_target | target_id | target_value
15 | 1 | a | 1 | Number of transformers modeled in User RMR and Baseline RMR are the same | pass | building/transformers/.. | num_of_elements_equal_to | baseline | rmr | triplet_101 | building/transformers/..
15 | 1 | b | 1 | Number of transformers modeled in User RMR and Baseline RMR are the same | fail | building/transformers/.. | num_of_elements_equal_to | baseline | rmr | triplet_102 | building/transformers/..
15 | 6 | a | 1 | Transformer efficiency reported in User RMR equals Table 8.4.4 | pass | building/transformer/transformer/type | value_equal_to | user | self | triplet_101 | Drytype
15 | 6 | a | 2 | Transformer efficiency reported in User RMR equals Table 8.4.4 | pass | building/transformer/transformer/phase | value_equal_to | user | table | table_8.4.4 | transformer_efficiency