## Start
Project Name | XXXX
Simulation Number: | XXXX
Feeding Arangement: | XXXX
Modelled by: | XXXX
Date: | 2024-01-25
NOTE: CHANGE SETTINGS AND NOTE ACCORDINGLY. DO NOT CHANGE GRAY PART. |  |  |  | FOR INFORMATION ONLY. CHANGE DOES NOT AFFECT THE FINAL ASSESSED CRITERIA
Items | Description | Settings | Note | Items | Criteria
VISION OSLO MODEL | Modelled Supply Point Voltage (kV) | 26.25 | VO Setting | PCC Maximum Voltage (kV) | 138.6
| Modelled time increament (s) | 5 | VO Setting | PCC Minimum Voltage (kV) | 118.8
| Supply Point OSLO ID | BRF1 | Market Harborough | PCC 1-min Maximum S (MVA) - Apparent | 100
|  |  |  | PCC 10-min Maximum S (MVA) - Apparent | -
GRID INFORMATION | Norminal Voltage (kV) | 132 | Market Harborough Grid | PCC 30-min Maximum S (MVA) - Apparent | 40
| Max Operating Range (kV) [Grid Code ECC. 6.1.4] | 5% | Grid Code | PCC 1-min Maximum Q (MVAr) - Reactive | 43.2731
| Min Operating Range (kV) [Grid Code ECC. 6.1.4] | -10% | Grid Code | PCC 10-min Maximum Q (MVAr) - Reactive | -
| Minimum Three Phase Symmetric Fault Level (MVA) | 10000 | Grid ETYS | PCC 30-min Maximum Q (MVAr) -Reactive | 17.3092
|  |  |  | PCC 1-min Negative Phase Sequence (NPS) | 2%
GRID BILATERAL AGREEMENT | 1-min maximum average loading (MVA) [Appendix F5] | 100 | Power Modelling | PCC 10-min Negative Phase Sequence (NPS) | -
| 10-min maximum average loading (MVA) [Appendix F5] |  | Power Modelling | PCC 30-min Negative Phase Sequence (NPS) | 1%
| 30-min maximum average loading (MVA) [Appendix F5] | 40 | Power Modelling | PCC Step Voltage Change (SVC) | 3%
|  |  |  | PCC Rapid Voltage Change (RVC) - Frequent Event | 6%
RVC EVENT (USER DEFINED) | Maximum Current (A) at 25 kV - Frequent Event [ECC. 6.1.7] | 800 | single RS passing NS | PCC RVC - Infrequenty Event | 10%
| Maximum Current (A) at 25 kV - Infrequent Event [ECC. 6.1.7] | 2727 | Network Energisation | PCC RVC - Very Infrequent Event | 12%
| Maximum Current (A) at 25 kV - Very infrequent Event [ECC. 6.1.7] | 1600 | 2 RS passing NS | Flicker Severity - Short Term RVC with Pst <= 0.5 | 0.6%
|  |  |  | Flicker Severity - Memory Time Technique (S) | 600
|  |  |  | Flicker Severity - Long Term | Stage 2 Pass
[6 empty] | NPS (%) | 1-min. | #REF! | 2 %
[7 empty] | 10-min. | #REF! | 2 %
[7 empty] | 30-min. | #REF! | 1 %
[6 empty] | Q (MVAr) | 1-min. | #REF! | #REF!
[7 empty] | 30-min. | #REF! | #REF!
[6 empty] | PF | 1-min. | #REF! | 0.9
[7 empty] | 30-min. | #REF!