## Start
Project Name | XXXX
Simulation Number: | XXXX
Feeding Arangement: | XXXX
Modelled by: | XXXX
Date: | 2024-01-24
NOTE: Adjust settings highlighted in Orange if necessary
Location | OLE Section | OSLO ID | Type | OLE Type | Cont. Rating (A) | 20min (A) | 10min (A) | 5min (A) | Note | Enviroment | Source
Substation A | Substation A - Substation B: Up Main Line | 005B/E | Mark 1 | GEFF | 700 | - | - | 957 | 700A for nominal, 964A with wind 3 m/s, 957A for 5 min | 30 C with wind 0.4 m/s | GEFF System Desciption Manual, Section 3.3
Substation B | Substation A - Substation B: Down Main Line | 007B/S | UKMS 107 CuSn | Mark GE | 800 | - | - | - | 800A for nominal, 400A for tramway |  | NR/L2/ELP/21088
|  |  |  | Mark SCS | 700 | - | - | - | 700A for support 0.166 in CW, 800A for support 0.3 in CW | - | MkSCS Equipment Designation
|  |  |  | Mark 1 | 700 | - | - | - | 800A for compound, 700A for simple, 400A for tramway | - | Mk1 Equipment Designations
|  |  |  | BBC | 700 | - | - | - | 700A for nominal | - | NR/L2/ELP/21088
|  |  |  | Mark 2 | 700 | - | - | - | 700A for nominal | - | NR/L2/ELP/21088
|  |  |  | Mark 3 | 700 | - | - | - | 700A for nominal, 400A for tramway | - | Mk3 Equipment Designation
|  |  |  | Mark 3a | 600 | - | - | - | 600A for nominal, 400A for tramway | - | Mk 3A Equipment Designation
|  |  |  | Mark 3b | 450 | - | - | - | 450A for 1 or 2 track or 4 track CS, 370A for 4 track BT | 28 C with wind 1 mph | Current Rating of Mark 3B OLE
|  |  |  | Mark 3c | 600 | - | - | - | 600A for nominal | - | Mk 3C Equipment Designation
|  |  |  | Mark 3d | 600 | - | - | - | 600A for nominal | - | NR/L2/ELP/21088
|  |  |  | Mark 5 | 900 | - | - | - | 900A for nominal | - | NR/L2/ELP/21088
|  |  |  | UK1 - WCML | 600 | - | - | - | 600A for nominal | - | NR/L2/ELP/21088
|  |  |  | Sunderland Direct | 779 | - | - | - | 779A for nominal | - | NR/L2/ELP/21088
|  |  |  | SICAT OLE | 600 | - | - | - | 600A for nominal | - | NR/L2/ELP/21088
|  |  |  | UK Series 1 | 531 | - | - | - | 531A for CW, 761A for ATF wire | 28 C with wind 1 mph, solar 980 W/m2 | MAN001 System Description Manual
|  |  |  | UK Series 2 | 533 | - | - | - | 533A for CuSn, 551A for CuAg, 590A for CuAg 120 | BS EN 50119:2009 | Series 2 System Description Manual
|  |  |  | UKMS 120 CuAg | 430 | 524 | 638 | 798 | Refer source - current revision 5 | 40 C with wind 1 mph | MS/B01/B01/A3 Revision 05
|  |  |  | UKMS 107 CuAg | 412 | 494 | 598 | 746 | Refer source - current revision 5 | 40 C with wind 1 mph | MS/B01/B01/A3 Revision 05
|  |  |  | UKMS 107 CuSn | 391 | 467 | 565 | 705 | Refer source - current revision 5 | 40 C with wind 1 mph | MS/B01/B01/A3 Revision 05